## tank slab (hidden)
Sindri sump pump house tank slab
Tank slab
CALCULATION OF B.M IN SLAB
|  |  |  | 0.078 |  | 0.102 | Wl2
0.046
[5 empty] | 0.078 | *Wl2
| l = | 1.55 | M
|  |  |  | w | = | 0.5 | t/sqm
Moment at ist Support |  |  | = | 0.12253 | t-m/m
Moment at 1st Span |  |  | = | 0.093698 | t-m/m
Moment at int Support |  |  | = | 0.093698 | t-m/m
Moment at int Span |  |  | = | 0.055258 | t-m/m
|  | Depth of slab | = | 175 | mm
|  | Effective Depth | = | 150 | mm
|  | Yield Stress of Reinf |  | 500 | n/mm2
Reinf as per Table-2,Pg-48,SP-16
| Reqd. reinf | Mu/bd2 | ptxd/10 |  | Reqd |  | %of Reinf
For -ve moment i.e. top reinf. 1st supp |  | 0.081685 | 0.12 | (0.12*1000*150)/100) | 180 | cm2/m | 0.12
For +ve moment 1st span |  | 0.062465 | 0.12 | (0.12*1000*)/100) | 180 | cm2/m | 0.12
0.12
For -ve moment i.e. top reinf. int supp |  | 0.062465 | 0.12 | (0.12*1000*)/100) | 180 | cm2/m | 0.12
For +ve moment int span |  | 0.036838 | 0.12 | (0.12*1000*)/100) | 180 | cm2/m | 0.12
| Main Reinforcements | F | spacing
For -ve moment i.e. top reinf. 1st supp |  | 8 | 200 | = pi/4*(8/10)^2*1000/200 = | 251.4286 | cm2/m | 0.16762 | TRUE
For +ve moment 1st span |  | 8 | 200 | = pi/4*(8/10)^2*1000/200 = | 251.4286 | cm2/m | 0.16762 | TRUE
For -ve moment i.e. top reinf. int supp |  | 8 | 200 | = pi/4*(8/10)^2*1000/200 = | 251.4286 | cm2/m | 0.16762 | TRUE
For +ve moment intspan |  | 8 | 200 | = pi/4*(8/10)^2*1000/200 = | 251.4286 | cm2/m | 0.16762 | TRUE
0.16762
C. DEFLECTION CHECK
| Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
|  |  |  | Cantilever | 7
|  |  |  | Simply supported | 20
|  |  |  | Continuous | 26
| fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 207.614
| Multiplication factor corresponding to steel service stress of 0.168% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 2
| Modified applicable ratio assuming 'Discontinuous' |  |  | = 26*2 = | 52
| Actual 'Span' to 'Depth' ratio |  |  | = 1550/150 = | 10.3333
OK from deflection considerations.
Single Span
|  |  | span | 3000
0.125
[5 empty] | load | 0.84 | t/sqm
Moment at 1st Span |  |  | = | 0.945 | t-m/m
|  | Depth of slab | = | 135 | mm
|  | Effective Depth | = | 110 | mm
|  | Yield Stress of Reinf |  | 500 | n/mm2
Reinf as per Table-2,Pg-48,SP-16
| Reqd. reinf | Mu/bd2 | ptxd/10 |  | Reqd |  | %of Reinf
For +ve moment 1st span |  | 1.1715 | 0.2852 | (0.2852*1000*110)/100) | 313.72 | cm2/m | 0.2852
| Main Reinforcements | F | spacing
For -ve moment i.e. top reinf. 1st supp |  | 8 | 130 | = pi/4*(8/10)^2*1000/130 = | 386.8132 | cm2/m | 0.35165 | TRUE
C. DEFLECTION CHECK
| Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
|  |  |  | Cantilever | 7
|  |  |  | Simply supported | 20
|  |  |  | Continuous | 26
| fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 235.201
| Multiplication factor corresponding to steel service stress of 0.352% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 1.4313
| Modified applicable ratio assuming 'Discontinuous' |  |  | = 20*1.43 = | 28.626
| Actual 'Span' to 'Depth' ratio |  |  | = 3000/110 = | 27.2727
OK from deflection considerations.

## main
STRUCTURE : |  | ADMIN BUILDING | [12 empty] | Pt | M25 | Mu/bd2(fck-25) | fy-500 |  |  |  | Mu/bd2(fck-25) | FE 415
ITEM : |  | S5 | [14 empty] | 0 | 0.12 |  |  |  | 0.01 | 0.084
[17 empty] | 0.17 | 0.1032 |  |  |  | 0.35 | 0.099
[17 empty] | 0.18 | 0.1056 |  |  |  | 0.4 | 0.113
[9 empty] | 1 | Interior Panel | 1 | [5 empty] | 0.19 | 0.108 |  |  |  | 0.45 | 0.127
| Longer clear span |  | = |  | 6000 |  |  |  | 2 | One Short Edge Discontinuous | 2 | [5 empty] | 0.2 | 0.1104 |  |  |  | 0.5 | 0.142
[9 empty] | 3 | One Long Edge Discontinuous | 3 | [5 empty] | 0.21 | 0.1128 |  |  |  | 0.55 | 0.156
| Sorter clear span |  | = |  | 5000 |  |  |  | 4 | Two Adjacent Edges Discontinuous | 4 | [5 empty] | 0.22 | 0.1152 |  |  |  | 0.6 | 0.171
[9 empty] | 5 | 5 Two short edge disc. | 5 | [5 empty] | 0.23 | 0.1176 |  |  |  | 0.65 | 0.186
| Thickness of Slab |  | = |  | 200 |  |  |  | 6 | 6 Two long. edge disc. | 6 | 0 |  |  |  |  | 0.24 | 0.12 |  |  |  | 0.7 | 0.201
[9 empty] | 7 | 7 Three edge disc.(one Long edge cont.) | 7 | 0 |  |  |  |  | 0.25 | 0.12 |  |  |  | 0.75 | 0.216
| Total UDL. |  | = |  | 1.4 |  |  |  | 8 | 8 Three edge disc.(one short edge cont.) | 8 | 0 |  |  |  |  | 0.26 | 0.12 |  |  |  | 0.8 | 0.231
[9 empty] | 9 | Four Edges Discontinuous | 9 | [5 empty] | 0.27 | 0.12 |  |  |  | 0.85 | 0.246
| Support Condition |  | = |  | Interior Panel | [11 empty] | 0.28 | 0.12 |  |  |  | 0.9 | 0.261
[17 empty] | 0.29 | 0.12 |  |  |  | 0.95 | 0.276
| A. DESIGN FORCES | [13 empty] | 0.15 | 0.29 | 0.3 | 0.12 |  |  |  | 1 | 0.291
| Longer clear span |  |  |  | 6000 | <mm; m> | 6 | One Short Edge Discontinuous | [6 empty] | 0.16 | 0.297 | 0.31 | 0.12 |  |  |  | 1.05 | 0.307
| Sorter clear span |  |  |  | 5000 | <mm; m> | 5 | 1 | [6 empty] | 0.17 | 0.304 | 0.32 | 0.12 |  |  |  | 1.1 | 0.322
[9 empty] | 0 | 0 | 0 |  |  |  | 0.18 | 0.311 | 0.33 | 0.12 |  |  |  | 1.15 | 0.338
| Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 200 | <mm; m> | 0.2 |  | 8 | 300 | 1.67 |  |  |  | 0.19 | 0.318 | 0.34 | 0.12 |  |  |  | 1.2 | 0.353
| Clear cover to main reinf |  |  |  | 30 | mm |  |  | 8 | 250 | 2 |  |  |  | 0.2 | 0.325 | 0.35 | 0.12 |  |  |  | 1.25 | 0.369
| Maximum diameter of bar |  |  |  | 10 | mm |  |  | 8 | 225 | 2.23 |  |  |  | 0.21 | 0.332 | 0.36 | 0.12 |  |  |  | 1.3 | 0.385
| Facor of safety |  | Reinf |  | 1.5 | mm |  |  | 8 | 200 | 2.51 |  |  |  | 0.22 | 0.339 | 0.37 | 0.12 |  |  |  | 1.35 | 0.401
| minimum slab thkness |  |  |  | 110 | mm |  |  | 10 | 300 | 2.61 |  |  |  | 0.23 | 0.346 | 0.38 | 0.12 |  |  |  | 1.4 | 0.417
| Permissible Mu/bd2 |  |  |  | 2.76 |  |  |  | 8 | 175 | 2.87 |  |  |  | 0.24 | 0.353 | 0.39 | 0.12 |  |  |  | 1.45 | 0.433
|  | OK,More than the min. as per tender. | [6 empty] | 10 | 250 | 3.14 |  |  |  | 0.25 | 0.36 | 0.4 | 0.12 |  |  |  | 1.5 | 0.449
|  | OK, From max. Mu/bd2 considerations as detailed hereunder. | [6 empty] | 8 | 150 | 3.34 |  |  |  | 0.26 | 0.3652 | 0.41 | 0.12 |  |  |  | 1.55 | 0.466
|  | OK from deflection considerations as checked hereunder. | [6 empty] | 10 | 225 | 3.48 |  |  |  | 0.27 | 0.3704 | 0.42 | 0.12 |  |  |  | 1.6 | 0.482
| The least effective depth in shorter / longer direction |  |  | = 200-30 -10/2 = | 165 | <mm; cm> | 16.5 |  | 12 | 300 | 3.76 |  |  |  | 0.28 | 0.3756 | 0.43 | 0.12 |  |  |  | 1.65 | 0.499
[9 empty] | 10 | 200 | 3.92 |  |  |  | 0.29 | 0.3808 | 0.44 | 0.12 |  |  |  | 1.7 | 0.515
| Total design UDL |  |  |  | 1.4 | t/m2 |  |  | 8 | 125 | 4.01 |  |  |  | 0.3 | 0.386 | 0.45 | 0.12 |  |  |  | 1.75 | 0.532
|  |  |  | Say | 1.4 | t/m2 |  |  | 10 | 175 | 4.48 |  |  |  | 0.31 | 0.3912 | 0.46 | 0.12 |  |  |  | 1.8 | 0.549
[9 empty] | 12 | 250 | 4.52 |  |  |  | 0.32 | 0.3964 | 0.47 | 0.12 |  |  |  | 1.85 | 0.566
| Longer effective span | LY |  | = 6000+165 = | 6165 | <mm; m> | 6.165 |  | 8 | 100 | 5.02 |  |  |  | 0.33 | 0.4016 | 0.48 | 0.12 |  |  |  | 1.9 | 0.583
| Sorter effective span | Lx |  | = 5000+165 = | 5165 | <mm; m> | 5.165 |  | 12 | 225 | 5.02 |  |  |  | 0.34 | 0.4068 | 0.49 | 0.12 |  |  |  | 1.95 | 0.601
|  |  | Ly/Lx | = 6165/5165 = | 1.19 |  |  |  | 10 | 150 | 5.23 |  |  |  | 0.35 | 0.412 | 0.5 | 0.118 |  |  |  | 2 | 0.618
[9 empty] | 12 | 200 | 5.65 |  |  |  | 0.36 | 0.4172 | 0.51 | 0.1204 |  |  |  | 2.05 | 0.635
| Shorter of the two spans (for use in bending moment calculations) |  |  |  | 5165 | <mm; m> | 5.165 |  | 10 | 125 | 6.28 |  |  |  | 0.37 | 0.4224 | 0.52 | 0.1228 |  |  |  | 2.1 | 0.653
[9 empty] | 12 | 175 | 6.45 |  |  |  | 0.38 | 0.4276 | 0.53 | 0.1252
| Refering IS-456, Table-22, P91 |  | 1 | Interior Panel |  |  |  |  | 16 | 300 | 6.69 |  |  |  | 0.39 | 0.4328 | 0.54 | 0.1276
| -ve support moment at continuous edge across long span | -My | 0.0424 | = 0.042*1.4*5.17^2 = | 1.5836 | tm |  | 1.5836 | 12 | 150 | 7.53 |  |  |  | 0.4 | 0.438 | 0.55 | 0.13
| +ve moment at mid span across long span | +My | 0.0316 | = 0.032*1.4*5.17^2 = | 1.1802 | tm |  |  | 10 | 100 | 7.85 |  |  |  | 0.41 | 0.4432 | 0.56 | 0.1324
| -ve support moment at continuous edge across short span | -Mx | 0.032 | = 0.032*1.4*5.17^2 = | 1.1951 | tm |  |  | 16 | 250 | 8.03 |  |  |  | 0.42 | 0.4484 | 0.57 | 0.1348
| +ve moment at mid span across short span | +Mx | 0.024 | = 0.024*1.4*5.17^2 = | 0.89635 | tm |  |  | 16 | 225 | 8.93 |  |  |  | 0.43 | 0.4536 | 0.58 | 0.1372
[9 empty] | 12 | 125 | 9.04 |  |  |  | 0.44 | 0.4588 | 0.59 | 0.1396
| B. REINFORCEMENTS | [7 empty] | 16 | 200 | 10.04 |  |  |  | 0.45 | 0.464 | 0.6 | 0.142
| -ve Mu/bd2 at support across long span |  | = 1.5*1.58*10000/165^2 = |  | 0.87248 | N/mm2 |  |  | 10 | 75 | 10.46 |  |  |  | 0.46 | 0.4692 | 0.61 | 0.1444
| +ve Mu/bd2 at mid span across long span |  | = 1.5*1.18*10000/165^2 = |  | 0.65025 | N/mm2 |  |  | 20 | 300 | 10.46 |  |  |  | 0.47 | 0.4744 | 0.62 | 0.1468
| -ve Mu/bd2 at support across short span |  | = 1.5*1.2*10000/165^2 = |  | 0.65848 | N/mm2 |  |  | 12 | 100 | 11.3 |  |  |  | 0.48 | 0.4796 | 0.63 | 0.1492
| +ve Mu/bd2 at mid span across short span |  | = 1.5*0.9*10000/165^2 = |  | 0.49386 | N/mm2 |  |  | 16 | 175 | 11.48 |  |  |  | 0.49 | 0.4848 | 0.64 | 0.1516
[9 empty] | 20 | 250 | 12.56 |  |  |  | 0.5 | 0.49 | 0.65 | 0.154
| Max. Mu/bd2 |  |  | Max. of (0.87:0.49) | 0.87248 | N/mm2 |  |  | 16 | 150 | 13.39 |  |  |  | 0.51 | 0.4932 | 0.66 | 0.1566
| Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456 | [7 empty] | 20 | 225 | 13.95 |  |  |  | 0.52 | 0.4964 | 0.67 | 0.1592
| 0.12 |  |  | = 0.0012*16.5*100 = | 1.98 | cm2/m |  |  | 12 | 75 | 15.07 |  |  |  | 0.53 | 0.4996 | 0.68 | 0.1618
[9 empty] | 20 | 200 | 15.7 |  |  |  | 0.54 | 0.5028 | 0.69 | 0.1644
|  |  | Reinf as per Table-2,Pg-48,SP-16 | [5 empty] | 16 | 125 | 16.07 |  |  |  | 0.55 | 0.506 | 0.7 | 0.167
| Reqd. reinf | Mu/bd2 | ptxd/10 | [5 empty] | 25 | 300 | 16.35 |  |  |  | 0.56 | 0.5092 | 0.71 | 0.1696
[9 empty] | 20 | 175 | 17.94 |  |  |  | 0.57 | 0.5124 | 0.72 | 0.1722
| For -ve moment i.e. top reinf. across long span | 0.87248 | 0.2088 | = 0.209*16.5/10 = | 3.45 | cm2/m |  |  | 25 | 250 | 19.62 |  |  |  | 0.58 | 0.5156 | 0.73 | 0.1748
| For +ve moment i.e. bottom reinf. across long span | 0.65025 | 0.154 | = 0.154*16.5/10 = | 2.55 | cm2/m |  |  | 16 | 100 | 20.09 |  |  |  | 0.59 | 0.5188 | 0.74 | 0.1774
| For -ve moment i.e. top reinf. across short span | 0.65848 | 0.154 | = 0.154*16.5/10 = | 2.55 | cm2/m |  |  | 20 | 150 | 20.93 |  |  |  | 0.6 | 0.522 | 0.75 | 0.179
| For +ve moment i.e. bottom reinf. across short span | 0.49386 | 0.12 | = 0.12*16.5/10 = | 1.98 | cm2/m |  |  | 25 | 225 | 21.8 |  |  |  | 0.61 | 0.5252 | 0.76 | 0.1814
[9 empty] | 25 | 200 | 24.53 |  |  |  | 0.62 | 0.5284 | 0.77 | 0.1838
| Main Reinforcements | F | spacing | [5 empty] | 20 | 125 | 25.12 |  |  |  | 0.63 | 0.5316 | 0.78 | 0.1862
| At top across long span | 10 | 225 | = pi/4*(10/10)^2*1000/225 = | 3.4921 | cm2/m | 0.212 |  | 16 | 75 | 26.79 |  |  |  | 0.64 | 0.5348 | 0.79 | 0.1886
| At bottom across long span | 10 | 300 | = pi/4*(10/10)^2*1000/300 = | 2.619 | cm2/m | 0.159 |  | 25 | 175 | 28.03 |  |  |  | 0.65 | 0.538 | 0.8 | 0.191
| At top across short span | 10 | 300 | = pi/4*(10/10)^2*1000/300 = | 2.619 | cm2/m | 0.159 |  | 20 | 100 | 31.4 |  |  |  | 0.66 | 0.5412 | 0.81 | 0.1936
| At bottom across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.122 |  | 25 | 150 | 32.7 |  |  |  | 0.67 | 0.5444 | 0.82 | 0.1962
[5 empty] | Max. % steel = |  | 0.212 |  | 25 | 125 | 39.25 |  |  |  | 0.68 | 0.5476 | 0.83 | 0.1988
| Max. permissible spacing | 3 | 495 | (As per Cl. 26.3.3; Pg. 46; IS:456) |  |  |  |  | 20 | 75 | 41.86 |  |  |  | 0.69 | 0.5508 | 0.84 | 0.2014
|  | or | 300 | [5 empty] | 25 | 100 | 49.06 |  |  |  | 0.7 | 0.554 | 0.85 | 0.204
| Least of the two |  | 300 | [5 empty] | 25 | 75 | 65.41 |  |  |  | 0.71 | 0.5572 | 0.86 | 0.2064
| Max. provided spacing |  | 300 | [11 empty] | 0.72 | 0.5604 | 0.87 | 0.2088
|  |  | OK | [11 empty] | 0.73 | 0.5636 | 0.88 | 0.2112
| Distribution Reinforcement | [13 empty] | 0.74 | 0.5668 | 0.89 | 0.2136
| Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456 | [13 empty] | 0.75 | 0.57 | 0.9 | 0.216
| 0.12 |  |  | = 0.0012*16.5*100 = | 1.98 | cm2/m | [8 empty] | 0.76 | 0.5728 | 0.91 | 0.2186
| Provide | 8 | 300 | = pi/4*(8/10)^2*1000/300 = | 1.6762 | cm2/m | [8 empty] | 0.77 | 0.5756 | 0.92 | 0.2212
| Max. permissible spacing | 5 | 825 | (As per Cl. 26.3.3; Pg. 46; IS:456) | [10 empty] | 0.78 | 0.5784 | 0.93 | 0.2238
|  | or | 450 | [11 empty] | 0.79 | 0.5812 | 0.94 | 0.2264
| Least of the two |  | 450 | [11 empty] | 0.8 | 0.584 | 0.95 | 0.229
| Max. provided spacing |  | 300 | [11 empty] | 0.81 | 0.5868 | 0.96 | 0.2316
|  |  | OK | [11 empty] | 0.82 | 0.5896 | 0.97 | 0.2342
| C. DEFLECTION CHECK | [13 empty] | 0.83 | 0.5924 | 0.98 | 0.2368
| Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456) | [11 empty] | 0.84 | 0.5952 | 0.99 | 0.2394
|  |  |  | Cantilever | 7 | [9 empty] | 0.85 | 0.598 | 1 | 0.242
|  |  |  | Simply supported | 20 | [9 empty] | 0.86 | 0.6008 | 1.01 | 0.2446
|  |  |  | Continuous | 26 | [9 empty] | 0.87 | 0.6036 | 1.02 | 0.2472
| fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 286.5068 | [9 empty] | 0.88 | 0.6064 | 1.03 | 0.2498
| Multiplication factor corresponding to steel service stress of 0.212% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 1.3764 | [9 empty] | 0.89 | 0.6092 | 1.04 | 0.2524
| Modified applicable ratio assuming 'Discontinuous' |  |  | = 1.38*26 = | 35.7874 | [9 empty] | 0.9 | 0.612 | 1.05 | 0.255
| Actual 'Span' to 'Depth' ratio |  |  | = 5000/165 = | 30.303 | [9 empty] | 0.91 | 0.6148 | 1.06 | 0.2574
|  | OK from deflection considerations. | [12 empty] | 0.92 | 0.6176 | 1.07 | 0.2598
[15 empty] | 0.93 | 0.6204 | 1.08 | 0.2622
| D. SKETCH | [13 empty] | 0.94 | 0.6232 | 1.09 | 0.2646
[15 empty] | 0.95 | 0.626 | 1.1 | 0.267
|  |  |  | 10 | 225 | [9 empty] | 0.96 | 0.6288 | 1.11 | 0.2696
[15 empty] | 0.97 | 0.6316 | 1.12 | 0.2722
|  |  | 10 | 300 | [10 empty] | 0.98 | 0.6344 | 1.13 | 0.2748
[15 empty] | 0.99 | 0.6372 | 1.14 | 0.2774
| 5000 | [13 empty] | 1 | 0.64 | 1.15 | 0.28
[5 empty] | 10 | 300 | [10 empty] | 1.16 | 0.2826
|  |  | 8 | 250 | [12 empty] | 1.17 | 0.2852
[17 empty] | 1.18 | 0.2878
[17 empty] | 1.19 | 0.2904
|  | 6000 | [14 empty] | 1.2 | 0.293
|  |  | PLAN | [13 empty] | 1.21 | 0.2956
[17 empty] | 1.22 | 0.2982
|  | All distribution rebars = | 8 | 300 | [12 empty] | 1.23 | 0.3008
[17 empty] | 1.24 | 0.3034
[17 empty] | 1.25 | 0.306
[6 empty] | 200 | [10 empty] | 1.26 | 0.3088
[17 empty] | 1.27 | 0.3116
[17 empty] | 1.28 | 0.3144
|  |  | SECTION | [13 empty] | 1.29 | 0.3172
[17 empty] | 1.3 | 0.32
| Provided rebars on drawings may be the same or greater than the above design requirements. | [15 empty] | 1.31 | 0.3226
[17 empty] | 1.32 | 0.3252
[17 empty] | 1.33 | 0.3278
[17 empty] | 1.34 | 0.3304
114 | [16 empty] | 1.35 | 0.333
115 | [16 empty] | 1.36 | 0.3356
[17 empty] | 1.37 | 0.3382
[17 empty] | 1.38 | 0.3408
[17 empty] | 1.39 | 0.3434
[17 empty] | 1.4 | 0.346
[17 empty] | 1.41 | 0.3486
[17 empty] | 1.42 | 0.3512
[17 empty] | 1.43 | 0.3538
[17 empty] | 1.44 | 0.3564
[17 empty] | 1.45 | 0.359
[17 empty] | 1.46 | 0.3618
[17 empty] | 1.47 | 0.3646
[17 empty] | 1.48 | 0.3674
[17 empty] | 1.49 | 0.3702
[17 empty] | 1.5 | 0.373
[17 empty] | 1.51 | 0.3758
[17 empty] | 1.52 | 0.3786
[17 empty] | 1.53 | 0.3814
[17 empty] | 1.54 | 0.3842
[17 empty] | 1.55 | 0.387
[17 empty] | 1.56 | 0.3896
[17 empty] | 1.57 | 0.3922
[17 empty] | 1.58 | 0.3948
[17 empty] | 1.59 | 0.3974
[17 empty] | 1.6 | 0.4
[17 empty] | 1.61 | 0.4028
[17 empty] | 1.62 | 0.4056
[17 empty] | 1.63 | 0.4084
[17 empty] | 1.64 | 0.4112
[17 empty] | 1.65 | 0.414
[17 empty] | 1.66 | 0.4168
[17 empty] | 1.67 | 0.4196
[17 empty] | 1.68 | 0.4224
[17 empty] | 1.69 | 0.4252
[17 empty] | 1.7 | 0.428
[17 empty] | 1.71 | 0.4308
[17 empty] | 1.72 | 0.4336
[17 empty] | 1.73 | 0.4364
[17 empty] | 1.74 | 0.4392
[17 empty] | 1.75 | 0.442
[17 empty] | 1.76 | 0.4448
[17 empty] | 1.77 | 0.4476
[17 empty] | 1.78 | 0.4504
[17 empty] | 1.79 | 0.4532
[17 empty] | 1.8 | 0.456
[17 empty] | 1.81 | 0.4588
[17 empty] | 1.82 | 0.4616
[17 empty] | 1.83 | 0.4644
[17 empty] | 1.84 | 0.4672
[17 empty] | 1.85 | 0.47
[17 empty] | 1.86 | 0.4728
[17 empty] | 1.87 | 0.4756
[17 empty] | 1.88 | 0.4784
[17 empty] | 1.89 | 0.4812
[17 empty] | 1.9 | 0.484
[17 empty] | 1.91 | 0.4868
[17 empty] | 1.92 | 0.4896
[17 empty] | 1.93 | 0.4924
[17 empty] | 1.94 | 0.4952
[17 empty] | 1.95 | 0.498
[17 empty] | 1.96 | 0.501
[17 empty] | 1.97 | 0.504
[17 empty] | 1.98 | 0.507
[17 empty] | 1.99 | 0.51
[17 empty] | 2 | 0.513
[17 empty] | 2.01 | 0.5158
[17 empty] | 2.02 | 0.5186
[17 empty] | 2.03 | 0.5214
[17 empty] | 2.04 | 0.5242
[17 empty] | 2.05 | 0.527
[17 empty] | 2.06 | 0.53
[17 empty] | 2.07 | 0.533
[17 empty] | 2.08 | 0.536
[17 empty] | 2.09 | 0.539
[17 empty] | 2.1 | 0.542
[17 empty] | 2.11 | 0.545
[17 empty] | 2.12 | 0.548
[17 empty] | 2.13 | 0.551
[17 empty] | 2.14 | 0.554
[17 empty] | 2.15 | 0.557
[17 empty] | 2.16 | 0.56
[17 empty] | 2.17 | 0.563
[17 empty] | 2.18 | 0.566
[17 empty] | 2.19 | 0.569
[17 empty] | 2.2 | 0.572
[17 empty] | 2.21 | 0.575
[17 empty] | 2.22 | 0.578
[17 empty] | 2.23 | 0.581
[17 empty] | 2.24 | 0.584
[17 empty] | 2.25 | 0.587
[17 empty] | 2.26 | 0.59
[17 empty] | 2.27 | 0.593
[17 empty] | 2.28 | 0.596
[17 empty] | 2.29 | 0.599
[17 empty] | 2.3 | 0.602
[17 empty] | 2.31 | 0.605
[17 empty] | 2.32 | 0.608
[17 empty] | 2.33 | 0.611
[17 empty] | 2.34 | 0.614
[17 empty] | 2.35 | 0.617
[17 empty] | 2.36 | 0.62
[17 empty] | 2.37 | 0.623
[17 empty] | 2.38 | 0.626
[17 empty] | 2.39 | 0.629
[17 empty] | 2.4 | 0.632
[17 empty] | 2.41 | 0.6352
[17 empty] | 2.42 | 0.6384
[17 empty] | 2.43 | 0.6416
[17 empty] | 2.44 | 0.6448
[17 empty] | 2.45 | 0.648
[17 empty] | 2.46 | 0.651
[17 empty] | 2.47 | 0.654
[17 empty] | 2.48 | 0.657
[17 empty] | 2.49 | 0.66
[17 empty] | 2.5 | 0.663
[17 empty] | 2.51 | 0.6662
[17 empty] | 2.52 | 0.6694
[17 empty] | 2.53 | 0.6726
[17 empty] | 2.54 | 0.6758
[17 empty] | 2.55 | 0.679
[17 empty] | 2.56 | 0.6822
[17 empty] | 2.57 | 0.6854
[17 empty] | 2.58 | 0.6886
[17 empty] | 2.59 | 0.6918
[17 empty] | 2.6 | 0.695
[17 empty] | 2.61 | 0.6982
[17 empty] | 2.62 | 0.7014
[17 empty] | 2.63 | 0.7046
[17 empty] | 2.64 | 0.7078
[17 empty] | 2.65 | 0.711
[17 empty] | 2.66 | 0.7142
[17 empty] | 2.67 | 0.7174
[17 empty] | 2.68 | 0.7206
[17 empty] | 2.69 | 0.7238
[17 empty] | 2.7 | 0.727
[17 empty] | 2.71 | 0.7304
[17 empty] | 2.72 | 0.7338
[17 empty] | 2.73 | 0.7372
[17 empty] | 2.74 | 0.7406
[17 empty] | 2.75 | 0.744
[17 empty] | 2.76 | 0.7472
[17 empty] | 2.77 | 0.7504
[17 empty] | 2.78 | 0.7536
[17 empty] | 2.79 | 0.7568
[17 empty] | 2.8 | 0.76
[17 empty] | 2.81 | 0.7634
[17 empty] | 2.82 | 0.7668
[17 empty] | 2.83 | 0.7702
[17 empty] | 2.84 | 0.7736
[17 empty] | 2.85 | 0.777
[17 empty] | 2.86 | 0.7804
[17 empty] | 2.87 | 0.7838
[17 empty] | 2.88 | 0.7872
[17 empty] | 2.89 | 0.7906
[17 empty] | 2.9 | 0.794
[17 empty] | 2.91 | 0.7974
[17 empty] | 2.92 | 0.8008
[17 empty] | 2.93 | 0.8042
[17 empty] | 2.94 | 0.8076
[17 empty] | 2.95 | 0.811
[17 empty] | 2.96 | 0.8144
[17 empty] | 2.97 | 0.8178
[17 empty] | 2.98 | 0.8212
[17 empty] | 2.99 | 0.8246
[17 empty] | 3 | 0.828
[17 empty] | 3.01 | 0.8314
[17 empty] | 3.02 | 0.8348
[17 empty] | 3.03 | 0.8382
[17 empty] | 3.04 | 0.8416
[17 empty] | 3.05 | 0.845
[17 empty] | 3.06 | 0.8486
[17 empty] | 3.07 | 0.8522
[17 empty] | 3.08 | 0.8558
[17 empty] | 3.09 | 0.8594
[17 empty] | 3.1 | 0.863
[17 empty] | 3.11 | 0.8664
[17 empty] | 3.12 | 0.8698
[17 empty] | 3.13 | 0.8732
[17 empty] | 3.14 | 0.8766
[17 empty] | 3.15 | 0.88
[17 empty] | 3.16 | 0.8836
[17 empty] | 3.17 | 0.8872
[17 empty] | 3.18 | 0.8908
[17 empty] | 3.19 | 0.8944
[17 empty] | 3.2 | 0.898
[17 empty] | 3.21 | 0.9016
[17 empty] | 3.22 | 0.9052
[17 empty] | 3.23 | 0.9088
[17 empty] | 3.24 | 0.9124
[17 empty] | 3.25 | 0.916
[17 empty] | 3.26 | 0.9198
[17 empty] | 3.27 | 0.9236
[17 empty] | 3.28 | 0.9274
[17 empty] | 3.29 | 0.9312
[17 empty] | 3.3 | 0.935
[17 empty] | 3.31 | 0.9388
[17 empty] | 3.32 | 0.9426
[14 empty] | CASE |  | 1 | 1.01 | 1.02 | 1.03 | 1.04 | 1.05 | 1.06 | 1.07 | 1.08 | 1.09 | 1.1 | 1.11 | 1.12 | 1.13 | 1.14 | 1.15 | 1.16 | 1.17 | 1.18 | 1.19 | 1.2 | 1.21 | 1.22 | 1.23 | 1.24 | 1.25 | 1.26 | 1.27 | 1.28 | 1.29 | 1.3 | 1.31 | 1.32 | 1.33 | 1.34 | 1.35 | 1.36 | 1.37 | 1.38 | 1.39 | 1.4 | 1.41 | 1.42 | 1.43 | 1.44 | 1.45 | 1.46 | 1.47 | 1.48 | 1.49 | 1.5 | 1.51 | 1.52 | 1.53 | 1.54 | 1.55 | 1.56 | 1.57 | 1.58 | 1.59 | 1.6 | 1.61 | 1.62 | 1.63 | 1.64 | 1.65 | 1.66 | 1.67 | 1.68 | 1.69 | 1.7 | 1.71 | 1.72 | 1.73 | 1.74 | 1.75 | 1.76 | 1.77 | 1.78 | 1.79 | 1.8 | 1.81 | 1.82 | 1.83 | 1.84 | 1.85 | 1.86 | 1.87 | 1.88 | 1.89 | 1.9 | 1.91 | 1.92 | 1.93 | 1.94 | 1.95 | 1.96 | 1.97 | 1.98 | 1.99 | 2
[14 empty] | 1 | - | 0.032 | 0.0325 | 0.033 | 0.0335 | 0.034 | 0.0345 | 0.035 | 0.0355 | 0.036 | 0.0365 | 0.037 | 0.0376 | 0.0382 | 0.0388 | 0.0394 | 0.04 | 0.0406 | 0.0412 | 0.0418 | 0.0424 | 0.043 | 0.0434 | 0.0438 | 0.0442 | 0.0446 | 0.045 | 0.0454 | 0.0458 | 0.0462 | 0.0466 | 0.047 | 0.0474 | 0.0478 | 0.0482 | 0.0486 | 0.049 | 0.0494 | 0.0498 | 0.0502 | 0.0506 | 0.051 | 0.0512 | 0.0514 | 0.0516 | 0.0518 | 0.052 | 0.0522 | 0.0524 | 0.0526 | 0.0528 | 0.053 | 0.05328 | 0.05356 | 0.05384 | 0.05412 | 0.0544 | 0.05468 | 0.05496 | 0.05524 | 0.05552 | 0.0558 | 0.05608 | 0.05636 | 0.05664 | 0.05692 | 0.0572 | 0.05748 | 0.05776 | 0.05804 | 0.05832 | 0.0586 | 0.05888 | 0.05916 | 0.05944 | 0.05972 | 0.06 | 0.0602 | 0.0604 | 0.0606 | 0.0608 | 0.061 | 0.0612 | 0.0614 | 0.0616 | 0.0618 | 0.062 | 0.0622 | 0.0624 | 0.0626 | 0.0628 | 0.063 | 0.0632 | 0.0634 | 0.0636 | 0.0638 | 0.064 | 0.0642 | 0.0644 | 0.0646 | 0.0648 | 0.065 |  | 0.032
[15 empty] | + | 0.024 | 0.0244 | 0.0248 | 0.0252 | 0.0256 | 0.026 | 0.0264 | 0.0268 | 0.0272 | 0.0276 | 0.028 | 0.0284 | 0.0288 | 0.0292 | 0.0296 | 0.03 | 0.0304 | 0.0308 | 0.0312 | 0.0316 | 0.032 | 0.0324 | 0.0328 | 0.0332 | 0.0336 | 0.034 | 0.0344 | 0.0348 | 0.0352 | 0.0356 | 0.036 | 0.0363 | 0.0366 | 0.0369 | 0.0372 | 0.0375 | 0.0378 | 0.0381 | 0.0384 | 0.0387 | 0.039 | 0.0392 | 0.0394 | 0.0396 | 0.0398 | 0.04 | 0.0402 | 0.0404 | 0.0406 | 0.0408 | 0.041 | 0.04116 | 0.04132 | 0.04148 | 0.04164 | 0.0418 | 0.04196 | 0.04212 | 0.04228 | 0.04244 | 0.0426 | 0.04276 | 0.04292 | 0.04308 | 0.04324 | 0.0434 | 0.04356 | 0.04372 | 0.04388 | 0.04404 | 0.0442 | 0.04436 | 0.04452 | 0.04468 | 0.04484 | 0.045 | 0.04516 | 0.04532 | 0.04548 | 0.04564 | 0.0458 | 0.04596 | 0.04612 | 0.04628 | 0.04644 | 0.0466 | 0.04676 | 0.04692 | 0.04708 | 0.04724 | 0.0474 | 0.04756 | 0.04772 | 0.04788 | 0.04804 | 0.0482 | 0.04836 | 0.04852 | 0.04868 | 0.04884 | 0.049 |  | 0.024
[14 empty] | 2 | - | 0.037 | 0.0376 | 0.0382 | 0.0388 | 0.0394 | 0.04 | 0.0406 | 0.0412 | 0.0418 | 0.0424 | 0.043 | 0.0435 | 0.044 | 0.0445 | 0.045 | 0.0455 | 0.046 | 0.0465 | 0.047 | 0.0475 | 0.048 | 0.0483 | 0.0486 | 0.0489 | 0.0492 | 0.0495 | 0.0498 | 0.0501 | 0.0504 | 0.0507 | 0.051 | 0.0514 | 0.0518 | 0.0522 | 0.0526 | 0.053 | 0.0534 | 0.0538 | 0.0542 | 0.0546 | 0.055 | 0.0552 | 0.0554 | 0.0556 | 0.0558 | 0.056 | 0.0562 | 0.0564 | 0.0566 | 0.0568 | 0.057 | 0.05728 | 0.05756 | 0.05784 | 0.05812 | 0.0584 | 0.05868 | 0.05896 | 0.05924 | 0.05952 | 0.0598 | 0.06008 | 0.06036 | 0.06064 | 0.06092 | 0.0612 | 0.06148 | 0.06176 | 0.06204 | 0.06232 | 0.0626 | 0.06288 | 0.06316 | 0.06344 | 0.06372 | 0.064 | 0.06416 | 0.06432 | 0.06448 | 0.06464 | 0.0648 | 0.06496 | 0.06512 | 0.06528 | 0.06544 | 0.0656 | 0.06576 | 0.06592 | 0.06608 | 0.06624 | 0.0664 | 0.06656 | 0.06672 | 0.06688 | 0.06704 | 0.0672 | 0.06736 | 0.06752 | 0.06768 | 0.06784 | 0.068 |  | 0.037
[15 empty] | + | 0.028 | 0.0284 | 0.0288 | 0.0292 | 0.0296 | 0.03 | 0.0304 | 0.0308 | 0.0312 | 0.0316 | 0.032 | 0.0324 | 0.0328 | 0.0332 | 0.0336 | 0.034 | 0.0344 | 0.0348 | 0.0352 | 0.0356 | 0.036 | 0.0363 | 0.0366 | 0.0369 | 0.0372 | 0.0375 | 0.0378 | 0.0381 | 0.0384 | 0.0387 | 0.039 | 0.0392 | 0.0394 | 0.0396 | 0.0398 | 0.04 | 0.0402 | 0.0404 | 0.0406 | 0.0408 | 0.041 | 0.0413 | 0.0416 | 0.0419 | 0.0422 | 0.0425 | 0.0428 | 0.0431 | 0.0434 | 0.0437 | 0.044 | 0.04416 | 0.04432 | 0.04448 | 0.04464 | 0.0448 | 0.04496 | 0.04512 | 0.04528 | 0.04544 | 0.0456 | 0.04576 | 0.04592 | 0.04608 | 0.04624 | 0.0464 | 0.04656 | 0.04672 | 0.04688 | 0.04704 | 0.0472 | 0.04736 | 0.04752 | 0.04768 | 0.04784 | 0.048 | 0.04816 | 0.04832 | 0.04848 | 0.04864 | 0.0488 | 0.04896 | 0.04912 | 0.04928 | 0.04944 | 0.0496 | 0.04976 | 0.04992 | 0.05008 | 0.05024 | 0.0504 | 0.05056 | 0.05072 | 0.05088 | 0.05104 | 0.0512 | 0.05136 | 0.05152 | 0.05168 | 0.05184 | 0.052 |  | 0.028
[14 empty] | 3 | - | 0.037 | 0.0377 | 0.0384 | 0.0391 | 0.0398 | 0.0405 | 0.0412 | 0.0419 | 0.0426 | 0.0433 | 0.044 | 0.0448 | 0.0456 | 0.0464 | 0.0472 | 0.048 | 0.0488 | 0.0496 | 0.0504 | 0.0512 | 0.052 | 0.0525 | 0.053 | 0.0535 | 0.054 | 0.0545 | 0.055 | 0.0555 | 0.056 | 0.0565 | 0.057 | 0.0576 | 0.0582 | 0.0588 | 0.0594 | 0.06 | 0.0606 | 0.0612 | 0.0618 | 0.0624 | 0.063 | 0.0634 | 0.0638 | 0.0642 | 0.0646 | 0.065 | 0.0654 | 0.0658 | 0.0662 | 0.0666 | 0.067 | 0.0674 | 0.0678 | 0.0682 | 0.0686 | 0.069 | 0.0694 | 0.0698 | 0.0702 | 0.0706 | 0.071 | 0.0714 | 0.0718 | 0.0722 | 0.0726 | 0.073 | 0.0734 | 0.0738 | 0.0742 | 0.0746 | 0.075 | 0.0754 | 0.0758 | 0.0762 | 0.0766 | 0.077 | 0.07732 | 0.07764 | 0.07796 | 0.07828 | 0.0786 | 0.07892 | 0.07924 | 0.07956 | 0.07988 | 0.0802 | 0.08052 | 0.08084 | 0.08116 | 0.08148 | 0.0818 | 0.08212 | 0.08244 | 0.08276 | 0.08308 | 0.0834 | 0.08372 | 0.08404 | 0.08436 | 0.08468 | 0.085 |  | 0.037
[15 empty] | + | 0.028 | 0.0285 | 0.029 | 0.0295 | 0.03 | 0.0305 | 0.031 | 0.0315 | 0.032 | 0.0325 | 0.033 | 0.0336 | 0.0342 | 0.0348 | 0.0354 | 0.036 | 0.0366 | 0.0372 | 0.0378 | 0.0384 | 0.039 | 0.0395 | 0.04 | 0.0405 | 0.041 | 0.0415 | 0.042 | 0.0425 | 0.043 | 0.0435 | 0.044 | 0.0443 | 0.0446 | 0.0449 | 0.0452 | 0.0455 | 0.0458 | 0.0461 | 0.0464 | 0.0467 | 0.047 | 0.0474 | 0.0478 | 0.0482 | 0.0486 | 0.049 | 0.0494 | 0.0498 | 0.0502 | 0.0506 | 0.051 | 0.05132 | 0.05164 | 0.05196 | 0.05228 | 0.0526 | 0.05292 | 0.05324 | 0.05356 | 0.05388 | 0.0542 | 0.05452 | 0.05484 | 0.05516 | 0.05548 | 0.0558 | 0.05612 | 0.05644 | 0.05676 | 0.05708 | 0.0574 | 0.05772 | 0.05804 | 0.05836 | 0.05868 | 0.059 | 0.05924 | 0.05948 | 0.05972 | 0.05996 | 0.0602 | 0.06044 | 0.06068 | 0.06092 | 0.06116 | 0.0614 | 0.06164 | 0.06188 | 0.06212 | 0.06236 | 0.0626 | 0.06284 | 0.06308 | 0.06332 | 0.06356 | 0.0638 | 0.06404 | 0.06428 | 0.06452 | 0.06476 | 0.065 |  | 0.28
[14 empty] | 4 | - | 0.047 | 0.0476 | 0.0482 | 0.0488 | 0.0494 | 0.05 | 0.0506 | 0.0512 | 0.0518 | 0.0524 | 0.053 | 0.0537 | 0.0544 | 0.0551 | 0.0558 | 0.0565 | 0.0572 | 0.0579 | 0.0586 | 0.0593 | 0.06 | 0.0605 | 0.061 | 0.0615 | 0.062 | 0.0625 | 0.063 | 0.0635 | 0.064 | 0.0645 | 0.065 | 0.0656 | 0.0662 | 0.0668 | 0.0674 | 0.068 | 0.0686 | 0.0692 | 0.0698 | 0.0704 | 0.071 | 0.0714 | 0.0718 | 0.0722 | 0.0726 | 0.073 | 0.0734 | 0.0738 | 0.0742 | 0.0746 | 0.075 | 0.07536 | 0.07572 | 0.07608 | 0.07644 | 0.0768 | 0.07716 | 0.07752 | 0.07788 | 0.07824 | 0.0786 | 0.07896 | 0.07932 | 0.07968 | 0.08004 | 0.0804 | 0.08076 | 0.08112 | 0.08148 | 0.08184 | 0.0822 | 0.08256 | 0.08292 | 0.08328 | 0.08364 | 0.084 | 0.08428 | 0.08456 | 0.08484 | 0.08512 | 0.0854 | 0.08568 | 0.08596 | 0.08624 | 0.08652 | 0.0868 | 0.08708 | 0.08736 | 0.08764 | 0.08792 | 0.0882 | 0.08848 | 0.08876 | 0.08904 | 0.08932 | 0.0896 | 0.08988 | 0.09016 | 0.09044 | 0.09072 | 0.091 |  | 0.047
[15 empty] | + | 0.035 | 0.0355 | 0.036 | 0.0365 | 0.037 | 0.0375 | 0.038 | 0.0385 | 0.039 | 0.0395 | 0.04 | 0.0405 | 0.041 | 0.0415 | 0.042 | 0.0425 | 0.043 | 0.0435 | 0.044 | 0.0445 | 0.045 | 0.0454 | 0.0458 | 0.0462 | 0.0466 | 0.047 | 0.0474 | 0.0478 | 0.0482 | 0.0486 | 0.049 | 0.0494 | 0.0498 | 0.0502 | 0.0506 | 0.051 | 0.0514 | 0.0518 | 0.0522 | 0.0526 | 0.053 | 0.0533 | 0.0536 | 0.0539 | 0.0542 | 0.0545 | 0.0548 | 0.0551 | 0.0554 | 0.0557 | 0.056 | 0.05628 | 0.05656 | 0.05684 | 0.05712 | 0.0574 | 0.05768 | 0.05796 | 0.05824 | 0.05852 | 0.0588 | 0.05908 | 0.05936 | 0.05964 | 0.05992 | 0.0602 | 0.06048 | 0.06076 | 0.06104 | 0.06132 | 0.0616 | 0.06188 | 0.06216 | 0.06244 | 0.06272 | 0.063 | 0.06324 | 0.06348 | 0.06372 | 0.06396 | 0.0642 | 0.06444 | 0.06468 | 0.06492 | 0.06516 | 0.0654 | 0.06564 | 0.06588 | 0.06612 | 0.06636 | 0.0666 | 0.06684 | 0.06708 | 0.06732 | 0.06756 | 0.0678 | 0.06804 | 0.06828 | 0.06852 | 0.06876 | 0.069 |  | 0.035
[14 empty] | 5 | - | 0.045 | 0.0454 | 0.0458 | 0.0462 | 0.0466 | 0.047 | 0.0474 | 0.0478 | 0.0482 | 0.0486 | 0.049 | 0.0493 | 0.0496 | 0.0499 | 0.0502 | 0.0505 | 0.0508 | 0.0511 | 0.0514 | 0.0517 | 0.052 | 0.0524 | 0.0528 | 0.0532 | 0.0536 | 0.054 | 0.0544 | 0.0548 | 0.0552 | 0.0556 | 0.056 | 0.0563 | 0.0566 | 0.0569 | 0.0572 | 0.0575 | 0.0578 | 0.0581 | 0.0584 | 0.0587 | 0.059 | 0.0591 | 0.0592 | 0.0593 | 0.0594 | 0.0595 | 0.0596 | 0.0597 | 0.0598 | 0.0599 | 0.06 | 0.0602 | 0.0604 | 0.0606 | 0.0608 | 0.061 | 0.0612 | 0.0614 | 0.0616 | 0.0618 | 0.062 | 0.0622 | 0.0624 | 0.0626 | 0.0628 | 0.063 | 0.0632 | 0.0634 | 0.0636 | 0.0638 | 0.064 | 0.0642 | 0.0644 | 0.0646 | 0.0648 | 0.065 | 0.06516 | 0.06532 | 0.06548 | 0.06564 | 0.0658 | 0.06596 | 0.06612 | 0.06628 | 0.06644 | 0.0666 | 0.06676 | 0.06692 | 0.06708 | 0.06724 | 0.0674 | 0.06756 | 0.06772 | 0.06788 | 0.06804 | 0.0682 | 0.06836 | 0.06852 | 0.06868 | 0.06884 | 0.069
[15 empty] | + | 0.035 | 0.0352 | 0.0354 | 0.0356 | 0.0358 | 0.036 | 0.0362 | 0.0364 | 0.0366 | 0.0368 | 0.037 | 0.0373 | 0.0376 | 0.0379 | 0.0382 | 0.0385 | 0.0388 | 0.0391 | 0.0394 | 0.0397 | 0.04 | 0.0403 | 0.0406 | 0.0409 | 0.0412 | 0.0415 | 0.0418 | 0.0421 | 0.0424 | 0.0427 | 0.043 | 0.0431 | 0.0432 | 0.0433 | 0.0434 | 0.0435 | 0.0436 | 0.0437 | 0.0438 | 0.0439 | 0.044 | 0.0441 | 0.0442 | 0.0443 | 0.0444 | 0.0445 | 0.0446 | 0.0447 | 0.0448 | 0.0449 | 0.045 | 0.04516 | 0.04532 | 0.04548 | 0.04564 | 0.0458 | 0.04596 | 0.04612 | 0.04628 | 0.04644 | 0.0466 | 0.04676 | 0.04692 | 0.04708 | 0.04724 | 0.0474 | 0.04756 | 0.04772 | 0.04788 | 0.04804 | 0.0482 | 0.04836 | 0.04852 | 0.04868 | 0.04884 | 0.049 | 0.04912 | 0.04924 | 0.04936 | 0.04948 | 0.0496 | 0.04972 | 0.04984 | 0.04996 | 0.05008 | 0.0502 | 0.05032 | 0.05044 | 0.05056 | 0.05068 | 0.0508 | 0.05092 | 0.05104 | 0.05116 | 0.05128 | 0.0514 | 0.05152 | 0.05164 | 0.05176 | 0.05188 | 0.052 |  | 0.035
[14 empty] | 6 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045
[15 empty] | + | 0.035 | 0.0358 | 0.0366 | 0.0374 | 0.0382 | 0.039 | 0.0398 | 0.0406 | 0.0414 | 0.0422 | 0.043 | 0.0437 | 0.0444 | 0.0451 | 0.0458 | 0.0465 | 0.0472 | 0.0479 | 0.0486 | 0.0493 | 0.05 | 0.0507 | 0.0514 | 0.0521 | 0.0528 | 0.0535 | 0.0542 | 0.0549 | 0.0556 | 0.0563 | 0.057 | 0.0576 | 0.0582 | 0.0588 | 0.0594 | 0.06 | 0.0606 | 0.0612 | 0.0618 | 0.0624 | 0.063 | 0.0635 | 0.064 | 0.0645 | 0.065 | 0.0655 | 0.066 | 0.0665 | 0.067 | 0.0675 | 0.068 | 0.06848 | 0.06896 | 0.06944 | 0.06992 | 0.0704 | 0.07088 | 0.07136 | 0.07184 | 0.07232 | 0.0728 | 0.07328 | 0.07376 | 0.07424 | 0.07472 | 0.0752 | 0.07568 | 0.07616 | 0.07664 | 0.07712 | 0.0776 | 0.07808 | 0.07856 | 0.07904 | 0.07952 | 0.08 | 0.08032 | 0.08064 | 0.08096 | 0.08128 | 0.0816 | 0.08192 | 0.08224 | 0.08256 | 0.08288 | 0.0832 | 0.08352 | 0.08384 | 0.08416 | 0.08448 | 0.0848 | 0.08512 | 0.08544 | 0.08576 | 0.08608 | 0.0864 | 0.08672 | 0.08704 | 0.08736 | 0.08768 | 0.088 |  | 0.035
[14 empty] | 7 | - | 0.057 | 0.0577 | 0.0584 | 0.0591 | 0.0598 | 0.0605 | 0.0612 | 0.0619 | 0.0626 | 0.0633 | 0.064 | 0.0647 | 0.0654 | 0.0661 | 0.0668 | 0.0675 | 0.0682 | 0.0689 | 0.0696 | 0.0703 | 0.071 | 0.0715 | 0.072 | 0.0725 | 0.073 | 0.0735 | 0.074 | 0.0745 | 0.075 | 0.0755 | 0.076 | 0.0764 | 0.0768 | 0.0772 | 0.0776 | 0.078 | 0.0784 | 0.0788 | 0.0792 | 0.0796 | 0.08 | 0.0804 | 0.0808 | 0.0812 | 0.0816 | 0.082 | 0.0824 | 0.0828 | 0.0832 | 0.0836 | 0.084 | 0.08428 | 0.08456 | 0.08484 | 0.08512 | 0.0854 | 0.08568 | 0.08596 | 0.08624 | 0.08652 | 0.0868 | 0.08708 | 0.08736 | 0.08764 | 0.08792 | 0.0882 | 0.08848 | 0.08876 | 0.08904 | 0.08932 | 0.0896 | 0.08988 | 0.09016 | 0.09044 | 0.09072 | 0.091 | 0.09124 | 0.09148 | 0.09172 | 0.09196 | 0.0922 | 0.09244 | 0.09268 | 0.09292 | 0.09316 | 0.0934 | 0.09364 | 0.09388 | 0.09412 | 0.09436 | 0.0946 | 0.09484 | 0.09508 | 0.09532 | 0.09556 | 0.0958 | 0.09604 | 0.09628 | 0.09652 | 0.09676 | 0.097
[15 empty] | + | 0.043 | 0.0435 | 0.044 | 0.0445 | 0.045 | 0.0455 | 0.046 | 0.0465 | 0.047 | 0.0475 | 0.048 | 0.0485 | 0.049 | 0.0495 | 0.05 | 0.0505 | 0.051 | 0.0515 | 0.052 | 0.0525 | 0.053 | 0.0534 | 0.0538 | 0.0542 | 0.0546 | 0.055 | 0.0554 | 0.0558 | 0.0562 | 0.0566 | 0.057 | 0.0573 | 0.0576 | 0.0579 | 0.0582 | 0.0585 | 0.0588 | 0.0591 | 0.0594 | 0.0597 | 0.06 | 0.0604 | 0.0608 | 0.0612 | 0.0616 | 0.062 | 0.0624 | 0.0628 | 0.0632 | 0.0636 | 0.064 | 0.0642 | 0.0644 | 0.0646 | 0.0648 | 0.065 | 0.0652 | 0.0654 | 0.0656 | 0.0658 | 0.066 | 0.0662 | 0.0664 | 0.0666 | 0.0668 | 0.067 | 0.0672 | 0.0674 | 0.0676 | 0.0678 | 0.068 | 0.0682 | 0.0684 | 0.0686 | 0.0688 | 0.069 | 0.06916 | 0.06932 | 0.06948 | 0.06964 | 0.0698 | 0.06996 | 0.07012 | 0.07028 | 0.07044 | 0.0706 | 0.07076 | 0.07092 | 0.07108 | 0.07124 | 0.0714 | 0.07156 | 0.07172 | 0.07188 | 0.07204 | 0.0722 | 0.07236 | 0.07252 | 0.07268 | 0.07284 | 0.073 |  | 0.043
[14 empty] | 8 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.057
[15 empty] | + | 0.043 | 0.0438 | 0.0446 | 0.0454 | 0.0462 | 0.047 | 0.0478 | 0.0486 | 0.0494 | 0.0502 | 0.051 | 0.0518 | 0.0526 | 0.0534 | 0.0542 | 0.055 | 0.0558 | 0.0566 | 0.0574 | 0.0582 | 0.059 | 0.0596 | 0.0602 | 0.0608 | 0.0614 | 0.062 | 0.0626 | 0.0632 | 0.0638 | 0.0644 | 0.065 | 0.0656 | 0.0662 | 0.0668 | 0.0674 | 0.068 | 0.0686 | 0.0692 | 0.0698 | 0.0704 | 0.071 | 0.0715 | 0.072 | 0.0725 | 0.073 | 0.0735 | 0.074 | 0.0745 | 0.075 | 0.0755 | 0.076 | 0.07644 | 0.07688 | 0.07732 | 0.07776 | 0.0782 | 0.07864 | 0.07908 | 0.07952 | 0.07996 | 0.0804 | 0.08084 | 0.08128 | 0.08172 | 0.08216 | 0.0826 | 0.08304 | 0.08348 | 0.08392 | 0.08436 | 0.0848 | 0.08524 | 0.08568 | 0.08612 | 0.08656 | 0.087 | 0.08736 | 0.08772 | 0.08808 | 0.08844 | 0.0888 | 0.08916 | 0.08952 | 0.08988 | 0.09024 | 0.0906 | 0.09096 | 0.09132 | 0.09168 | 0.09204 | 0.0924 | 0.09276 | 0.09312 | 0.09348 | 0.09384 | 0.0942 | 0.09456 | 0.09492 | 0.09528 | 0.09564 | 0.096 |  | 0.043
[14 empty] | 9 | - |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | + | 0.056 | 0.0568 | 0.0576 | 0.0584 | 0.0592 | 0.06 | 0.0608 | 0.0616 | 0.0624 | 0.0632 | 0.064 | 0.0648 | 0.0656 | 0.0664 | 0.0672 | 0.068 | 0.0688 | 0.0696 | 0.0704 | 0.0712 | 0.072 | 0.0727 | 0.0734 | 0.0741 | 0.0748 | 0.0755 | 0.0762 | 0.0769 | 0.0776 | 0.0783 | 0.079 | 0.0796 | 0.0802 | 0.0808 | 0.0814 | 0.082 | 0.0826 | 0.0832 | 0.0838 | 0.0844 | 0.085 | 0.0854 | 0.0858 | 0.0862 | 0.0866 | 0.087 | 0.0874 | 0.0878 | 0.0882 | 0.0886 | 0.089 | 0.08944 | 0.08988 | 0.09032 | 0.09076 | 0.0912 | 0.09164 | 0.09208 | 0.09252 | 0.09296 | 0.0934 | 0.09384 | 0.09428 | 0.09472 | 0.09516 | 0.0956 | 0.09604 | 0.09648 | 0.09692 | 0.09736 | 0.0978 | 0.09824 | 0.09868 | 0.09912 | 0.09956 | 0.1 | 0.10028 | 0.10056 | 0.10084 | 0.10112 | 0.1014 | 0.10168 | 0.10196 | 0.10224 | 0.10252 | 0.1028 | 0.10308 | 0.10336 | 0.10364 | 0.10392 | 0.1042 | 0.10448 | 0.10476 | 0.10504 | 0.10532 | 0.1056 | 0.10588 | 0.10616 | 0.10644 | 0.10672 | 0.107 |  | 0.056
-ve
[14 empty] | CASE |  |  | 1 | 1.01 | 1.02 | 1.03 | 1.04 | 1.05 | 1.06 | 1.07 | 1.08 | 1.09 | 1.1 | 1.11 | 1.12 | 1.13 | 1.14 | 1.15 | 1.16 | 1.17 | 1.18 | 1.19 | 1.2 | 1.21 | 1.22 | 1.23 | 1.24 | 1.25 | 1.26 | 1.27 | 1.28 | 1.29 | 1.3 | 1.31 | 1.32 | 1.33 | 1.34 | 1.35 | 1.36 | 1.37 | 1.38 | 1.39 | 1.4 | 1.41 | 1.42 | 1.43 | 1.44 | 1.45 | 1.46 | 1.47 | 1.48 | 1.49 | 1.5 | 1.51 | 1.52 | 1.53 | 1.54 | 1.55 | 1.56 | 1.57 | 1.58 | 1.59 | 1.6 | 1.61 | 1.62 | 1.63 | 1.64 | 1.65 | 1.66 | 1.67 | 1.68 | 1.69 | 1.7 | 1.71 | 1.72 | 1.73 | 1.74 | 1.75 | 1.76 | 1.77 | 1.78 | 1.79 | 1.8 | 1.81 | 1.82 | 1.83 | 1.84 | 1.85 | 1.86 | 1.87 | 1.88 | 1.89 | 1.9 | 1.91 | 1.92 | 1.93 | 1.94 | 1.95 | 1.96 | 1.97 | 1.98 | 1.99 | 2 |  | CASE
[14 empty] | 1 | - | 1 | 0.032 | 0.0325 | 0.033 | 0.0335 | 0.034 | 0.0345 | 0.035 | 0.0355 | 0.036 | 0.0365 | 0.037 | 0.0376 | 0.0382 | 0.0388 | 0.0394 | 0.04 | 0.0406 | 0.0412 | 0.0418 | 0.0424 | 0.043 | 0.0434 | 0.0438 | 0.0442 | 0.0446 | 0.045 | 0.0454 | 0.0458 | 0.0462 | 0.0466 | 0.047 | 0.0474 | 0.0478 | 0.0482 | 0.0486 | 0.049 | 0.0494 | 0.0498 | 0.0502 | 0.0506 | 0.051 | 0.0512 | 0.0514 | 0.0516 | 0.0518 | 0.052 | 0.0522 | 0.0524 | 0.0526 | 0.0528 | 0.053 | 0.05328 | 0.05356 | 0.05384 | 0.05412 | 0.0544 | 0.05468 | 0.05496 | 0.05524 | 0.05552 | 0.0558 | 0.05608 | 0.05636 | 0.05664 | 0.05692 | 0.0572 | 0.05748 | 0.05776 | 0.05804 | 0.05832 | 0.0586 | 0.05888 | 0.05916 | 0.05944 | 0.05972 | 0.06 | 0.0602 | 0.0604 | 0.0606 | 0.0608 | 0.061 | 0.0612 | 0.0614 | 0.0616 | 0.0618 | 0.062 | 0.0622 | 0.0624 | 0.0626 | 0.0628 | 0.063 | 0.0632 | 0.0634 | 0.0636 | 0.0638 | 0.064 | 0.0642 | 0.0644 | 0.0646 | 0.0648 | 0.065 |  | 1 | - | 0.032
[14 empty] | 2 | - | 2 | 0.037 | 0.0376 | 0.0382 | 0.0388 | 0.0394 | 0.04 | 0.0406 | 0.0412 | 0.0418 | 0.0424 | 0.043 | 0.0435 | 0.044 | 0.0445 | 0.045 | 0.0455 | 0.046 | 0.0465 | 0.047 | 0.0475 | 0.048 | 0.0483 | 0.0486 | 0.0489 | 0.0492 | 0.0495 | 0.0498 | 0.0501 | 0.0504 | 0.0507 | 0.051 | 0.0514 | 0.0518 | 0.0522 | 0.0526 | 0.053 | 0.0534 | 0.0538 | 0.0542 | 0.0546 | 0.055 | 0.0552 | 0.0554 | 0.0556 | 0.0558 | 0.056 | 0.0562 | 0.0564 | 0.0566 | 0.0568 | 0.057 | 0.05728 | 0.05756 | 0.05784 | 0.05812 | 0.0584 | 0.05868 | 0.05896 | 0.05924 | 0.05952 | 0.0598 | 0.06008 | 0.06036 | 0.06064 | 0.06092 | 0.0612 | 0.06148 | 0.06176 | 0.06204 | 0.06232 | 0.0626 | 0.06288 | 0.06316 | 0.06344 | 0.06372 | 0.064 | 0.06416 | 0.06432 | 0.06448 | 0.06464 | 0.0648 | 0.06496 | 0.06512 | 0.06528 | 0.06544 | 0.0656 | 0.06576 | 0.06592 | 0.06608 | 0.06624 | 0.0664 | 0.06656 | 0.06672 | 0.06688 | 0.06704 | 0.0672 | 0.06736 | 0.06752 | 0.06768 | 0.06784 | 0.068 |  | 2 | - | 0.037
[14 empty] | 3 | - | 3 | 0.037 | 0.0377 | 0.0384 | 0.0391 | 0.0398 | 0.0405 | 0.0412 | 0.0419 | 0.0426 | 0.0433 | 0.044 | 0.0448 | 0.0456 | 0.0464 | 0.0472 | 0.048 | 0.0488 | 0.0496 | 0.0504 | 0.0512 | 0.052 | 0.0525 | 0.053 | 0.0535 | 0.054 | 0.0545 | 0.055 | 0.0555 | 0.056 | 0.0565 | 0.057 | 0.0576 | 0.0582 | 0.0588 | 0.0594 | 0.06 | 0.0606 | 0.0612 | 0.0618 | 0.0624 | 0.063 | 0.0634 | 0.0638 | 0.0642 | 0.0646 | 0.065 | 0.0654 | 0.0658 | 0.0662 | 0.0666 | 0.067 | 0.0674 | 0.0678 | 0.0682 | 0.0686 | 0.069 | 0.0694 | 0.0698 | 0.0702 | 0.0706 | 0.071 | 0.0714 | 0.0718 | 0.0722 | 0.0726 | 0.073 | 0.0734 | 0.0738 | 0.0742 | 0.0746 | 0.075 | 0.0754 | 0.0758 | 0.0762 | 0.0766 | 0.077 | 0.07732 | 0.07764 | 0.07796 | 0.07828 | 0.0786 | 0.07892 | 0.07924 | 0.07956 | 0.07988 | 0.0802 | 0.08052 | 0.08084 | 0.08116 | 0.08148 | 0.0818 | 0.08212 | 0.08244 | 0.08276 | 0.08308 | 0.0834 | 0.08372 | 0.08404 | 0.08436 | 0.08468 | 0.085 |  | 3 | - | 0.037
[14 empty] | 4 | - | 4 | 0.047 | 0.0476 | 0.0482 | 0.0488 | 0.0494 | 0.05 | 0.0506 | 0.0512 | 0.0518 | 0.0524 | 0.053 | 0.0537 | 0.0544 | 0.0551 | 0.0558 | 0.0565 | 0.0572 | 0.0579 | 0.0586 | 0.0593 | 0.06 | 0.0605 | 0.061 | 0.0615 | 0.062 | 0.0625 | 0.063 | 0.0635 | 0.064 | 0.0645 | 0.065 | 0.0656 | 0.0662 | 0.0668 | 0.0674 | 0.068 | 0.0686 | 0.0692 | 0.0698 | 0.0704 | 0.071 | 0.0714 | 0.0718 | 0.0722 | 0.0726 | 0.073 | 0.0734 | 0.0738 | 0.0742 | 0.0746 | 0.075 | 0.07536 | 0.07572 | 0.07608 | 0.07644 | 0.0768 | 0.07716 | 0.07752 | 0.07788 | 0.07824 | 0.0786 | 0.07896 | 0.07932 | 0.07968 | 0.08004 | 0.0804 | 0.08076 | 0.08112 | 0.08148 | 0.08184 | 0.0822 | 0.08256 | 0.08292 | 0.08328 | 0.08364 | 0.084 | 0.08428 | 0.08456 | 0.08484 | 0.08512 | 0.0854 | 0.08568 | 0.08596 | 0.08624 | 0.08652 | 0.0868 | 0.08708 | 0.08736 | 0.08764 | 0.08792 | 0.0882 | 0.08848 | 0.08876 | 0.08904 | 0.08932 | 0.0896 | 0.08988 | 0.09016 | 0.09044 | 0.09072 | 0.091 |  | 4 | - | 0.047
[14 empty] | 5 | - | 5 | 0.045 | 0.0454 | 0.0458 | 0.0462 | 0.0466 | 0.047 | 0.0474 | 0.0478 | 0.0482 | 0.0486 | 0.049 | 0.0493 | 0.0496 | 0.0499 | 0.0502 | 0.0505 | 0.0508 | 0.0511 | 0.0514 | 0.0517 | 0.052 | 0.0524 | 0.0528 | 0.0532 | 0.0536 | 0.054 | 0.0544 | 0.0548 | 0.0552 | 0.0556 | 0.056 | 0.0563 | 0.0566 | 0.0569 | 0.0572 | 0.0575 | 0.0578 | 0.0581 | 0.0584 | 0.0587 | 0.059 | 0.0591 | 0.0592 | 0.0593 | 0.0594 | 0.0595 | 0.0596 | 0.0597 | 0.0598 | 0.0599 | 0.06 | 0.0602 | 0.0604 | 0.0606 | 0.0608 | 0.061 | 0.0612 | 0.0614 | 0.0616 | 0.0618 | 0.062 | 0.0622 | 0.0624 | 0.0626 | 0.0628 | 0.063 | 0.0632 | 0.0634 | 0.0636 | 0.0638 | 0.064 | 0.0642 | 0.0644 | 0.0646 | 0.0648 | 0.065 | 0.06516 | 0.06532 | 0.06548 | 0.06564 | 0.0658 | 0.06596 | 0.06612 | 0.06628 | 0.06644 | 0.0666 | 0.06676 | 0.06692 | 0.06708 | 0.06724 | 0.0674 | 0.06756 | 0.06772 | 0.06788 | 0.06804 | 0.0682 | 0.06836 | 0.06852 | 0.06868 | 0.06884 | 0.069 |  | 5 | - | 0
[14 empty] | 6 | - | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | - | 0.045
[14 empty] | 7 | - | 7 | 0.057 | 0.0577 | 0.0584 | 0.0591 | 0.0598 | 0.0605 | 0.0612 | 0.0619 | 0.0626 | 0.0633 | 0.064 | 0.0647 | 0.0654 | 0.0661 | 0.0668 | 0.0675 | 0.0682 | 0.0689 | 0.0696 | 0.0703 | 0.071 | 0.0715 | 0.072 | 0.0725 | 0.073 | 0.0735 | 0.074 | 0.0745 | 0.075 | 0.0755 | 0.076 | 0.0764 | 0.0768 | 0.0772 | 0.0776 | 0.078 | 0.0784 | 0.0788 | 0.0792 | 0.0796 | 0.08 | 0.0804 | 0.0808 | 0.0812 | 0.0816 | 0.082 | 0.0824 | 0.0828 | 0.0832 | 0.0836 | 0.084 | 0.08428 | 0.08456 | 0.08484 | 0.08512 | 0.0854 | 0.08568 | 0.08596 | 0.08624 | 0.08652 | 0.0868 | 0.08708 | 0.08736 | 0.08764 | 0.08792 | 0.0882 | 0.08848 | 0.08876 | 0.08904 | 0.08932 | 0.0896 | 0.08988 | 0.09016 | 0.09044 | 0.09072 | 0.091 | 0.09124 | 0.09148 | 0.09172 | 0.09196 | 0.0922 | 0.09244 | 0.09268 | 0.09292 | 0.09316 | 0.0934 | 0.09364 | 0.09388 | 0.09412 | 0.09436 | 0.0946 | 0.09484 | 0.09508 | 0.09532 | 0.09556 | 0.0958 | 0.09604 | 0.09628 | 0.09652 | 0.09676 | 0.097 |  | 7 | - | 0
[14 empty] | 8 | - | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | - | 0.057
[14 empty] | 9 | - | 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | - | 0
+ve
[14 empty] | CASE |  |  | 1 | 1.01 | 1.02 | 1.03 | 1.04 | 1.05 | 1.06 | 1.07 | 1.08 | 1.09 | 1.1 | 1.11 | 1.12 | 1.13 | 1.14 | 1.15 | 1.16 | 1.17 | 1.18 | 1.19 | 1.2 | 1.21 | 1.22 | 1.23 | 1.24 | 1.25 | 1.26 | 1.27 | 1.28 | 1.29 | 1.3 | 1.31 | 1.32 | 1.33 | 1.34 | 1.35 | 1.36 | 1.37 | 1.38 | 1.39 | 1.4 | 1.41 | 1.42 | 1.43 | 1.44 | 1.45 | 1.46 | 1.47 | 1.48 | 1.49 | 1.5 | 1.51 | 1.52 | 1.53 | 1.54 | 1.55 | 1.56 | 1.57 | 1.58 | 1.59 | 1.6 | 1.61 | 1.62 | 1.63 | 1.64 | 1.65 | 1.66 | 1.67 | 1.68 | 1.69 | 1.7 | 1.71 | 1.72 | 1.73 | 1.74 | 1.75 | 1.76 | 1.77 | 1.78 | 1.79 | 1.8 | 1.81 | 1.82 | 1.83 | 1.84 | 1.85 | 1.86 | 1.87 | 1.88 | 1.89 | 1.9 | 1.91 | 1.92 | 1.93 | 1.94 | 1.95 | 1.96 | 1.97 | 1.98 | 1.99 | 2 |  | CASE
[14 empty] | 1 | + | 1 | 0.024 | 0.0244 | 0.0248 | 0.0252 | 0.0256 | 0.026 | 0.0264 | 0.0268 | 0.0272 | 0.0276 | 0.028 | 0.0284 | 0.0288 | 0.0292 | 0.0296 | 0.03 | 0.0304 | 0.0308 | 0.0312 | 0.0316 | 0.032 | 0.0324 | 0.0328 | 0.0332 | 0.0336 | 0.034 | 0.0344 | 0.0348 | 0.0352 | 0.0356 | 0.036 | 0.0363 | 0.0366 | 0.0369 | 0.0372 | 0.0375 | 0.0378 | 0.0381 | 0.0384 | 0.0387 | 0.039 | 0.0392 | 0.0394 | 0.0396 | 0.0398 | 0.04 | 0.0402 | 0.0404 | 0.0406 | 0.0408 | 0.041 | 0.04116 | 0.04132 | 0.04148 | 0.04164 | 0.0418 | 0.04196 | 0.04212 | 0.04228 | 0.04244 | 0.0426 | 0.04276 | 0.04292 | 0.04308 | 0.04324 | 0.0434 | 0.04356 | 0.04372 | 0.04388 | 0.04404 | 0.0442 | 0.04436 | 0.04452 | 0.04468 | 0.04484 | 0.045 | 0.04516 | 0.04532 | 0.04548 | 0.04564 | 0.0458 | 0.04596 | 0.04612 | 0.04628 | 0.04644 | 0.0466 | 0.04676 | 0.04692 | 0.04708 | 0.04724 | 0.0474 | 0.04756 | 0.04772 | 0.04788 | 0.04804 | 0.0482 | 0.04836 | 0.04852 | 0.04868 | 0.04884 | 0.049 |  | 1 | + | 0.024
[14 empty] | 2 | + | 2 | 0.028 | 0.0284 | 0.0288 | 0.0292 | 0.0296 | 0.03 | 0.0304 | 0.0308 | 0.0312 | 0.0316 | 0.032 | 0.0324 | 0.0328 | 0.0332 | 0.0336 | 0.034 | 0.0344 | 0.0348 | 0.0352 | 0.0356 | 0.036 | 0.0363 | 0.0366 | 0.0369 | 0.0372 | 0.0375 | 0.0378 | 0.0381 | 0.0384 | 0.0387 | 0.039 | 0.0392 | 0.0394 | 0.0396 | 0.0398 | 0.04 | 0.0402 | 0.0404 | 0.0406 | 0.0408 | 0.041 | 0.0413 | 0.0416 | 0.0419 | 0.0422 | 0.0425 | 0.0428 | 0.0431 | 0.0434 | 0.0437 | 0.044 | 0.04416 | 0.04432 | 0.04448 | 0.04464 | 0.0448 | 0.04496 | 0.04512 | 0.04528 | 0.04544 | 0.0456 | 0.04576 | 0.04592 | 0.04608 | 0.04624 | 0.0464 | 0.04656 | 0.04672 | 0.04688 | 0.04704 | 0.0472 | 0.04736 | 0.04752 | 0.04768 | 0.04784 | 0.048 | 0.04816 | 0.04832 | 0.04848 | 0.04864 | 0.0488 | 0.04896 | 0.04912 | 0.04928 | 0.04944 | 0.0496 | 0.04976 | 0.04992 | 0.05008 | 0.05024 | 0.0504 | 0.05056 | 0.05072 | 0.05088 | 0.05104 | 0.0512 | 0.05136 | 0.05152 | 0.05168 | 0.05184 | 0.052 |  | 2 | + | 0.028
[14 empty] | 3 | + | 3 | 0.028 | 0.0285 | 0.029 | 0.0295 | 0.03 | 0.0305 | 0.031 | 0.0315 | 0.032 | 0.0325 | 0.033 | 0.0336 | 0.0342 | 0.0348 | 0.0354 | 0.036 | 0.0366 | 0.0372 | 0.0378 | 0.0384 | 0.039 | 0.0395 | 0.04 | 0.0405 | 0.041 | 0.0415 | 0.042 | 0.0425 | 0.043 | 0.0435 | 0.044 | 0.0443 | 0.0446 | 0.0449 | 0.0452 | 0.0455 | 0.0458 | 0.0461 | 0.0464 | 0.0467 | 0.047 | 0.0474 | 0.0478 | 0.0482 | 0.0486 | 0.049 | 0.0494 | 0.0498 | 0.0502 | 0.0506 | 0.051 | 0.05132 | 0.05164 | 0.05196 | 0.05228 | 0.0526 | 0.05292 | 0.05324 | 0.05356 | 0.05388 | 0.0542 | 0.05452 | 0.05484 | 0.05516 | 0.05548 | 0.0558 | 0.05612 | 0.05644 | 0.05676 | 0.05708 | 0.0574 | 0.05772 | 0.05804 | 0.05836 | 0.05868 | 0.059 | 0.05924 | 0.05948 | 0.05972 | 0.05996 | 0.0602 | 0.06044 | 0.06068 | 0.06092 | 0.06116 | 0.0614 | 0.06164 | 0.06188 | 0.06212 | 0.06236 | 0.0626 | 0.06284 | 0.06308 | 0.06332 | 0.06356 | 0.0638 | 0.06404 | 0.06428 | 0.06452 | 0.06476 | 0.065 |  | 3 | + | 0.028
[14 empty] | 4 | + | 4 | 0.035 | 0.0355 | 0.036 | 0.0365 | 0.037 | 0.0375 | 0.038 | 0.0385 | 0.039 | 0.0395 | 0.04 | 0.0405 | 0.041 | 0.0415 | 0.042 | 0.0425 | 0.043 | 0.0435 | 0.044 | 0.0445 | 0.045 | 0.0454 | 0.0458 | 0.0462 | 0.0466 | 0.047 | 0.0474 | 0.0478 | 0.0482 | 0.0486 | 0.049 | 0.0494 | 0.0498 | 0.0502 | 0.0506 | 0.051 | 0.0514 | 0.0518 | 0.0522 | 0.0526 | 0.053 | 0.0533 | 0.0536 | 0.0539 | 0.0542 | 0.0545 | 0.0548 | 0.0551 | 0.0554 | 0.0557 | 0.056 | 0.05628 | 0.05656 | 0.05684 | 0.05712 | 0.0574 | 0.05768 | 0.05796 | 0.05824 | 0.05852 | 0.0588 | 0.05908 | 0.05936 | 0.05964 | 0.05992 | 0.0602 | 0.06048 | 0.06076 | 0.06104 | 0.06132 | 0.0616 | 0.06188 | 0.06216 | 0.06244 | 0.06272 | 0.063 | 0.06324 | 0.06348 | 0.06372 | 0.06396 | 0.0642 | 0.06444 | 0.06468 | 0.06492 | 0.06516 | 0.0654 | 0.06564 | 0.06588 | 0.06612 | 0.06636 | 0.0666 | 0.06684 | 0.06708 | 0.06732 | 0.06756 | 0.0678 | 0.06804 | 0.06828 | 0.06852 | 0.06876 | 0.069 |  | 4 | + | 0.035
[14 empty] | 5 | + | 5 | 0.035 | 0.0352 | 0.0354 | 0.0356 | 0.0358 | 0.036 | 0.0362 | 0.0364 | 0.0366 | 0.0368 | 0.037 | 0.0373 | 0.0376 | 0.0379 | 0.0382 | 0.0385 | 0.0388 | 0.0391 | 0.0394 | 0.0397 | 0.04 | 0.0403 | 0.0406 | 0.0409 | 0.0412 | 0.0415 | 0.0418 | 0.0421 | 0.0424 | 0.0427 | 0.043 | 0.0431 | 0.0432 | 0.0433 | 0.0434 | 0.0435 | 0.0436 | 0.0437 | 0.0438 | 0.0439 | 0.044 | 0.0441 | 0.0442 | 0.0443 | 0.0444 | 0.0445 | 0.0446 | 0.0447 | 0.0448 | 0.0449 | 0.045 | 0.04516 | 0.04532 | 0.04548 | 0.04564 | 0.0458 | 0.04596 | 0.04612 | 0.04628 | 0.04644 | 0.0466 | 0.04676 | 0.04692 | 0.04708 | 0.04724 | 0.0474 | 0.04756 | 0.04772 | 0.04788 | 0.04804 | 0.0482 | 0.04836 | 0.04852 | 0.04868 | 0.04884 | 0.049 | 0.04912 | 0.04924 | 0.04936 | 0.04948 | 0.0496 | 0.04972 | 0.04984 | 0.04996 | 0.05008 | 0.0502 | 0.05032 | 0.05044 | 0.05056 | 0.05068 | 0.0508 | 0.05092 | 0.05104 | 0.05116 | 0.05128 | 0.0514 | 0.05152 | 0.05164 | 0.05176 | 0.05188 | 0.052 |  | 5 | + | 0.035
[14 empty] | 6 | + | 6 | 0.035 | 0.0358 | 0.0366 | 0.0374 | 0.0382 | 0.039 | 0.0398 | 0.0406 | 0.0414 | 0.0422 | 0.043 | 0.0437 | 0.0444 | 0.0451 | 0.0458 | 0.0465 | 0.0472 | 0.0479 | 0.0486 | 0.0493 | 0.05 | 0.0507 | 0.0514 | 0.0521 | 0.0528 | 0.0535 | 0.0542 | 0.0549 | 0.0556 | 0.0563 | 0.057 | 0.0576 | 0.0582 | 0.0588 | 0.0594 | 0.06 | 0.0606 | 0.0612 | 0.0618 | 0.0624 | 0.063 | 0.0635 | 0.064 | 0.0645 | 0.065 | 0.0655 | 0.066 | 0.0665 | 0.067 | 0.0675 | 0.068 | 0.06848 | 0.06896 | 0.06944 | 0.06992 | 0.0704 | 0.07088 | 0.07136 | 0.07184 | 0.07232 | 0.0728 | 0.07328 | 0.07376 | 0.07424 | 0.07472 | 0.0752 | 0.07568 | 0.07616 | 0.07664 | 0.07712 | 0.0776 | 0.07808 | 0.07856 | 0.07904 | 0.07952 | 0.08 | 0.08032 | 0.08064 | 0.08096 | 0.08128 | 0.0816 | 0.08192 | 0.08224 | 0.08256 | 0.08288 | 0.0832 | 0.08352 | 0.08384 | 0.08416 | 0.08448 | 0.0848 | 0.08512 | 0.08544 | 0.08576 | 0.08608 | 0.0864 | 0.08672 | 0.08704 | 0.08736 | 0.08768 | 0.088 |  | 6 | + | 0.035
[14 empty] | 7 | + | 7 | 0.043 | 0.0435 | 0.044 | 0.0445 | 0.045 | 0.0455 | 0.046 | 0.0465 | 0.047 | 0.0475 | 0.048 | 0.0485 | 0.049 | 0.0495 | 0.05 | 0.0505 | 0.051 | 0.0515 | 0.052 | 0.0525 | 0.053 | 0.0534 | 0.0538 | 0.0542 | 0.0546 | 0.055 | 0.0554 | 0.0558 | 0.0562 | 0.0566 | 0.057 | 0.0573 | 0.0576 | 0.0579 | 0.0582 | 0.0585 | 0.0588 | 0.0591 | 0.0594 | 0.0597 | 0.06 | 0.0604 | 0.0608 | 0.0612 | 0.0616 | 0.062 | 0.0624 | 0.0628 | 0.0632 | 0.0636 | 0.064 | 0.0642 | 0.0644 | 0.0646 | 0.0648 | 0.065 | 0.0652 | 0.0654 | 0.0656 | 0.0658 | 0.066 | 0.0662 | 0.0664 | 0.0666 | 0.0668 | 0.067 | 0.0672 | 0.0674 | 0.0676 | 0.0678 | 0.068 | 0.0682 | 0.0684 | 0.0686 | 0.0688 | 0.069 | 0.06916 | 0.06932 | 0.06948 | 0.06964 | 0.0698 | 0.06996 | 0.07012 | 0.07028 | 0.07044 | 0.0706 | 0.07076 | 0.07092 | 0.07108 | 0.07124 | 0.0714 | 0.07156 | 0.07172 | 0.07188 | 0.07204 | 0.0722 | 0.07236 | 0.07252 | 0.07268 | 0.07284 | 0.073 |  | 7 | + | 0.043
[14 empty] | 8 | + | 8 | 0.043 | 0.0438 | 0.0446 | 0.0454 | 0.0462 | 0.047 | 0.0478 | 0.0486 | 0.0494 | 0.0502 | 0.051 | 0.0518 | 0.0526 | 0.0534 | 0.0542 | 0.055 | 0.0558 | 0.0566 | 0.0574 | 0.0582 | 0.059 | 0.0596 | 0.0602 | 0.0608 | 0.0614 | 0.062 | 0.0626 | 0.0632 | 0.0638 | 0.0644 | 0.065 | 0.0656 | 0.0662 | 0.0668 | 0.0674 | 0.068 | 0.0686 | 0.0692 | 0.0698 | 0.0704 | 0.071 | 0.0715 | 0.072 | 0.0725 | 0.073 | 0.0735 | 0.074 | 0.0745 | 0.075 | 0.0755 | 0.076 | 0.07644 | 0.07688 | 0.07732 | 0.07776 | 0.0782 | 0.07864 | 0.07908 | 0.07952 | 0.07996 | 0.0804 | 0.08084 | 0.08128 | 0.08172 | 0.08216 | 0.0826 | 0.08304 | 0.08348 | 0.08392 | 0.08436 | 0.0848 | 0.08524 | 0.08568 | 0.08612 | 0.08656 | 0.087 | 0.08736 | 0.08772 | 0.08808 | 0.08844 | 0.0888 | 0.08916 | 0.08952 | 0.08988 | 0.09024 | 0.0906 | 0.09096 | 0.09132 | 0.09168 | 0.09204 | 0.0924 | 0.09276 | 0.09312 | 0.09348 | 0.09384 | 0.0942 | 0.09456 | 0.09492 | 0.09528 | 0.09564 | 0.096 |  | 8 | + | 0.043
[14 empty] | 9 | + | 9 | 0.056 | 0.0568 | 0.0576 | 0.0584 | 0.0592 | 0.06 | 0.0608 | 0.0616 | 0.0624 | 0.0632 | 0.064 | 0.0648 | 0.0656 | 0.0664 | 0.0672 | 0.068 | 0.0688 | 0.0696 | 0.0704 | 0.0712 | 0.072 | 0.0727 | 0.0734 | 0.0741 | 0.0748 | 0.0755 | 0.0762 | 0.0769 | 0.0776 | 0.0783 | 0.079 | 0.0796 | 0.0802 | 0.0808 | 0.0814 | 0.082 | 0.0826 | 0.0832 | 0.0838 | 0.0844 | 0.085 | 0.0854 | 0.0858 | 0.0862 | 0.0866 | 0.087 | 0.0874 | 0.0878 | 0.0882 | 0.0886 | 0.089 | 0.08944 | 0.08988 | 0.09032 | 0.09076 | 0.0912 | 0.09164 | 0.09208 | 0.09252 | 0.09296 | 0.0934 | 0.09384 | 0.09428 | 0.09472 | 0.09516 | 0.0956 | 0.09604 | 0.09648 | 0.09692 | 0.09736 | 0.0978 | 0.09824 | 0.09868 | 0.09912 | 0.09956 | 0.1 | 0.10028 | 0.10056 | 0.10084 | 0.10112 | 0.1014 | 0.10168 | 0.10196 | 0.10224 | 0.10252 | 0.1028 | 0.10308 | 0.10336 | 0.10364 | 0.10392 | 0.1042 | 0.10448 | 0.10476 | 0.10504 | 0.10532 | 0.1056 | 0.10588 | 0.10616 | 0.10644 | 0.10672 | 0.107 |  | 9 | + | 0.056

## S1 (hidden)
STRUCTURE : |  | ADMIN BUILDING
ITEM : |  | SLAB, S1 | [5 empty] | 1 | 1 Interior panel
Sl. No. | ITEM | NOTN. | FORMULA | CALCULATIONS | VALUE | UNIT | REMARKS | 2 | 2 one short edge disc.
[8 empty] | 3 | 3 one long edge disc.
A | B | C | D | E | F | G | H | 4 | 4 Two adjacent edge disc.
A: 1; B: Longer clear span; D: =; F: 4610 | 5 | 5 Two short edge disc.
[8 empty] | 6 | 6 Two long. edge disc.
A: 2; B: Sorter clear span; D: =; F: 2305 | 7 | 7 Three edge disc.(one Long edge cont.)
[8 empty] | 8 | 8 Three edge disc.(one short edge cont.)
A: 3; B: Thickness of Slab; D: =; F: 150 | 9 | 9 Four edge disc.
[10 empty] | 1 | 1 | Interior panel
A: 4; B: Total UDL.; D: =; F: 1.35 |  |  | 2 | 2 | one short edge disc.
[10 empty] | 3 | 3 | one long edge disc.
A: 5; B: Support Condition; D: =; F: 4 Two adjacent edge disc. |  |  | 4 | 4 | Two adjacent edge disc.
[10 empty] | 5 | 5 | Two short edge disc.
A: 8; B: A. DESIGN FORCES |  |  | 7 | 7 | Three edge disc.(one Long edge cont.)
9 | Longer clear span |  |  |  | 4610 | <mm; m> | 4.61 |  |  | 7 | 7 | Three edge disc.(one short edge cont.)
10 | Sorter clear span |  |  |  | 2305 | <mm; m> | 2.305 |  |  | 8 | 8 | Four edge disc.
11
12 | Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 150 | <mm; m> | 0.15
| Clear cover to main reinf |  |  |  | 25 | mm
| Maximum diameter of bar |  |  |  | 10 | mm
| Facor of safety |  |  |  | 1.5 | mm
| minimum slab thkness |  |  |  | 110 | mm
| Permissible Mu/bd2 |  |  |  | 2.76
13 |  | OK,More than the min. as per tender.
14 |  | OK, From max. Mu/bd2 considerations as detailed hereunder.
15 |  | OK from deflection considerations as checked hereunder.
16 | The least effective depth in shorter / longer direction |  |  | = 150-25 -10/2 = | 120 | <mm; cm> | 12
17
| Total design UDL |  |  |  | 1.35 | t/m2
19 |  |  |  | Say | 1.35 | t/m2
21
22 | Longer effective span | LY |  | = 4610+120 = | 4730 | <mm; m> | 4.73
23 | Sorter effective span | Lx |  | = 2305+120 = | 2425 | <mm; m> | 2.425
24 |  |  | Ly/Lx | = 4730/2425 = | 1.95
26
27 | Shorter of the two spans (for use in bending moment calculations) |  |  |  | 2425 | <mm; m> | 2.425
28
29 | Refering IS-456, Table-22, P91 |  | 4 | 4 Two adjacent edge disc.
30 | -ve support moment at continuous edge across long span | -My | 0.0896 | = 0.09*1.35*2.43^2 = | 0.71132 | tm
31 | +ve moment at mid span across long span | +My | 0.0678 | = 0.068*1.35*2.43^2 = | 0.53825 | tm
32 | -ve support moment at continuous edge across short span | -Mx | 0.047 | = 0.047*1.35*2.43^2 = | 0.37313 | tm
33 | +ve moment at mid span across short span | +Mx | 0.035 | = 0.035*1.35*2.43^2 = | 0.27786 | tm
34
35 | B. REINFORCEMENTS
36 | -ve Mu/bd2 at support across long span |  | = 1.5*0.71*10000/120^2 = |  | 0.74096 | N/mm2
37 | +ve Mu/bd2 at mid span across long span |  | = 1.5*0.54*10000/120^2 = |  | 0.56068 | N/mm2
38 | -ve Mu/bd2 at support across short span |  | = 1.5*0.37*10000/120^2 = |  | 0.38867 | N/mm2
39 | +ve Mu/bd2 at mid span across short span |  | = 1.5*0.28*10000/120^2 = |  | 0.28944 | N/mm2
40
41 | Max. Mu/bd2 |  |  | Max. of (0.74:0.29) | 0.74096 | N/mm2
44 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
45 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
46
47 |  |  | Reinf as per Table-2,Pg-48,SP-16
48 | Reqd. reinf | Mu/bd2 | ptxd/10
49
50 | For -ve moment i.e. top reinf. across long span | 0.74096 | 0.1774 | = 0.177*12/10 = | 2.1288 | cm2/m
51 | For +ve moment i.e. bottom reinf. across long span | 0.56068 | 0.1324 | = 0.132*12/10 = | 1.5888 | cm2/m
52 | For -ve moment i.e. top reinf. across short span | 0.38867 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
53 | For +ve moment i.e. bottom reinf. across short span | 0.28944 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
54
55 | Main Reinforcements | F | spacing
56 | At top across long span | 8 | 200 | = pi/4*(8/10)^2*1000/200 = | 2.5143 | cm2/m | 0.21
57 | At bottom across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
58 | At top across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
59 | At bottom across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
60 |  |  |  |  | Max. % steel = |  | 0.21
62 | Max. permissible spacing | 3 | 360 | (As per Cl. 26.3.3; Pg. 46; IS:456)
63 |  | or | 300
64 | Least of the two |  | 300
65 | Max. provided spacing |  | 250
66 |  |  | OK
68 | Distribution Reinforcement
69 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
70 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
71 | Provide | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m
72 | Max. permissible spacing | 5 | 600 | (As per Cl. 26.3.3; Pg. 46; IS:456)
73 |  | or | 450
74 | Least of the two |  | 450
75 | Max. provided spacing |  | 250
76 |  |  | OK
78 | C. DEFLECTION CHECK
79 | Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
80 |  |  |  | Cantilever | 7
81 |  |  |  | Simply supported | 20
82 |  |  |  | Continuous | 26
83 | fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 245.5377
| Multiplication factor corresponding to steel service stress of 0.21% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 1.6891
84 | Modified applicable ratio assuming 'Discontinuous' |  |  | = 1.69*26 = | 43.9175
85 | Actual 'Span' to 'Depth' ratio |  |  | = 2305/120 = | 19.2083
86 |  | OK from deflection considerations.
87
88 | D. SKETCH
89
90 |  |  |  | 8 | 200
91
92 |  |  | 8 | 250
93
94 | 2305
95 |  |  |  |  | 8 | 250
96 |  |  | 8 | 250
97
98
99 |  | 4610
100 |  |  | PLAN
101
102 |  | All distribution rebars = | 8 | 250
103
104
105 | [5 empty] | 150
106
107
108 |  |  | SECTION
109
110 | Provided rebars on drawings may be the same or greater than the above design requirements.
111
112
113
114
115

## S2 (hidden)
Slab-S2
CALCULATION OF B.M IN SLAB
|  |  |  | 0.078 |  | 0.102 | Wl2
0.046
[5 empty] | 0.078 | *Wl2
| l = | 1.41 | M
|  |  |  | w | = | 1.35 | t/sqm
Moment at ist Support |  |  | = | 0.27376 | t-m/m
Moment at 1st Span |  |  | = | 0.20935 | t-m/m
Moment at int Support |  |  | = | 0.20935 | t-m/m
Moment at int Span |  |  | = | 0.12346 | t-m/m
|  | Depth of slab | = | 150 | mm
|  | Effective Depth | = | 125 | mm
|  | Yield Stress of Reinf |  | 500 | n/mm2
Reinf as per Table-3,Pg-49,SP-16
| Reqd. reinf | Mu/bd2 | ptxd/10 |  | Reqd |  | %of Reinf
For -ve moment i.e. top reinf. 1st supp |  | 0.26281 | 0.12 | (0.12*1000*125)/100) | 150 | cm2/m | 0.12
For +ve moment 1st span |  | 0.20097 | 0.12 | (0.12*1000*)/100) | 150 | cm2/m | 0.12
For -ve moment i.e. top reinf. int supp |  | 0.20097 | 0.12 | (0.12*1000*)/100) | 150 | cm2/m | 0.12
For +ve moment int span |  | 0.11852 | 0.12 | (0.12*1000*)/100) | 150 | cm2/m | 0.12
| Main Reinforcements | F | spacing
For -ve moment i.e. top reinf. 1st supp |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
For +ve moment 1st span |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
For -ve moment i.e. top reinf. int supp |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
For +ve moment intspan |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
0.16091
C. DEFLECTION CHECK
| Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
|  |  |  | Cantilever | 7
|  |  |  | Simply supported | 20
|  |  |  | Continuous | 26
| fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 216.264
| Multiplication factor corresponding to steel service stress of 0.161% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 2
| Modified applicable ratio assuming 'Discontinuous' |  |  | = 26*2 = | 52
| Actual 'Span' to 'Depth' ratio |  |  | = 1410/125 = | 11.28
OK from deflection considerations.

## S3 (hidden)
STRUCTURE : |  | ADMIN BUILDING
ITEM : |  | SLAB, S1 | [5 empty] | 1 | 1 Interior panel
Sl. No. | ITEM | NOTN. | FORMULA | CALCULATIONS | VALUE | UNIT | REMARKS | 2 | 2 one short edge disc.
[8 empty] | 3 | 3 one long edge disc.
A | B | C | D | E | F | G | H | 4 | 4 Two adjacent edge disc.
A: 1; B: Longer clear span; D: =; F: 4610 | 5 | 5 Two short edge disc.
[8 empty] | 6 | 6 Two long. edge disc.
A: 2; B: Sorter clear span; D: =; F: 2305 | 7 | 7 Three edge disc.(one Long edge cont.)
[8 empty] | 8 | 8 Three edge disc.(one short edge cont.)
A: 3; B: Thickness of Slab; D: =; F: 175 | 9 | 9 Four edge disc.
[10 empty] | 1 | 1 | Interior panel
A: 4; B: Total UDL.; D: =; F: 1.4 |  |  | 2 | 2 | one short edge disc.
[10 empty] | 3 | 3 | one long edge disc.
A: 5; B: Support Condition; D: =; F: 7 Three edge disc.(one Long edge cont.) |  |  | 4 | 4 | Two adjacent edge disc.
[10 empty] | 5 | 5 | Two short edge disc.
A: 8; B: A. DESIGN FORCES |  |  | 7 | 7 | Three edge disc.(one Long edge cont.)
9 | Longer clear span |  |  |  | 4610 | <mm; m> | 4.61 |  |  | 7 | 7 | Three edge disc.(one short edge cont.)
10 | Sorter clear span |  |  |  | 2305 | <mm; m> | 2.305 |  |  | 8 | 8 | Four edge disc.
11
12 | Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 175 | <mm; m> | 0.175
| Clear cover to main reinf |  |  |  | 25 | mm
| Maximum diameter of bar |  |  |  | 10 | mm
| Facor of safety |  |  |  | 1.5 | mm
| minimum slab thkness |  |  |  | 110 | mm
| Permissible Mu/bd2 |  |  |  | 2.76
13 |  | OK,More than the min. as per tender.
14 |  | OK, From max. Mu/bd2 considerations as detailed hereunder.
15 |  | OK from deflection considerations as checked hereunder.
16 | The least effective depth in shorter / longer direction |  |  | = 175-25 -10/2 = | 145 | <mm; cm> | 14.5
17
| Total design UDL |  |  |  | 1.4 | t/m2
19 |  |  |  | Say | 1.4 | t/m2
21
22 | Longer effective span | LY |  | = 4610+145 = | 4755 | <mm; m> | 4.755
23 | Sorter effective span | Lx |  | = 2305+145 = | 2450 | <mm; m> | 2.45
24 |  |  | Ly/Lx | = 4755/2450 = | 1.94
26
27 | Shorter of the two spans (for use in bending moment calculations) |  |  |  | 2450 | <mm; m> | 2.45
28
29 | Refering IS-456, Table-22, P91 |  | 7 | 7 Three edge disc.(one Long edge cont.)
30 | -ve support moment at continuous edge across long span | -My | 0.09556 | = 0.096*1.4*2.45^2 = | 0.80304 | tm
31 | +ve moment at mid span across long span | +My | 0.07204 | = 0.072*1.4*2.45^2 = | 0.60539 | tm
32 | -ve support moment at continuous edge across short span | -Mx | 0 | = 0*1.4*2.45^2 = | 0 | tm
33 | +ve moment at mid span across short span | +Mx | 0.043 | = 0.043*1.4*2.45^2 = | 0.36135 | tm
34
35 | B. REINFORCEMENTS
36 | -ve Mu/bd2 at support across long span |  | = 1.5*0.8*10000/145^2 = |  | 0.57292 | N/mm2
37 | +ve Mu/bd2 at mid span across long span |  | = 1.5*0.61*10000/145^2 = |  | 0.43191 | N/mm2
38 | -ve Mu/bd2 at support across short span |  | = 1.5*0*10000/145^2 = |  | 0 | N/mm2
39 | +ve Mu/bd2 at mid span across short span |  | = 1.5*0.36*10000/145^2 = |  | 0.2578 | N/mm2
40
41 | Max. Mu/bd2 |  |  | Max. of (0.57:0.26) | 0.57292 | N/mm2
44 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
45 | 0.12 |  |  | = 0.0012*14.5*100 = | 1.74 | cm2/m
46
47 |  |  | Reinf as per Table-2,Pg-48,SP-16
48 | Reqd. reinf | Mu/bd2 | ptxd/10
49
50 | For -ve moment i.e. top reinf. across long span | 0.57292 | 0.1348 | = 0.135*14.5/10 = | 1.9546 | cm2/m
51 | For +ve moment i.e. bottom reinf. across long span | 0.43191 | 0.12 | = 0.12*14.5/10 = | 1.74 | cm2/m
52 | For -ve moment i.e. top reinf. across short span | 0 | 0.12 | = 0.12*14.5/10 = | 1.74 | cm2/m
53 | For +ve moment i.e. bottom reinf. across short span | 0.2578 | 0.12 | = 0.12*14.5/10 = | 1.74 | cm2/m
54
55 | Main Reinforcements | F | spacing
56 | At top across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.139
57 | At bottom across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.139
58 | At top across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.139
59 | At bottom across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.139
60 |  |  |  |  | Max. % steel = |  | 0.139
62 | Max. permissible spacing | 3 | 435 | (As per Cl. 26.3.3; Pg. 46; IS:456)
63 |  | or | 300
64 | Least of the two |  | 300
65 | Max. provided spacing |  | 250
66 |  |  | OK
68 | Distribution Reinforcement
69 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
70 | 0.12 |  |  | = 0.0012*14.5*100 = | 1.74 | cm2/m
71 | Provide | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m
72 | Max. permissible spacing | 5 | 725 | (As per Cl. 26.3.3; Pg. 46; IS:456)
73 |  | or | 450
74 | Least of the two |  | 450
75 | Max. provided spacing |  | 250
76 |  |  | OK
78 | C. DEFLECTION CHECK
79 | Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
80 |  |  |  | Cantilever | 7
81 |  |  |  | Simply supported | 20
82 |  |  |  | Continuous | 26
83 | fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 281.8067
| Multiplication factor corresponding to steel service stress of 0.139% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 1.6756
84 | Modified applicable ratio assuming 'Discontinuous' |  |  | = 1.68*26 = | 43.5656
85 | Actual 'Span' to 'Depth' ratio |  |  | = 2305/145 = | 15.8966
86 |  | OK from deflection considerations.
87
88 | D. SKETCH
89
90 |  |  |  | 8 | 250
91
92 |  |  | 8 | 250
93
94 | 2305
95 |  |  |  |  | 8 | 250
96 |  |  | 8 | 250
97
98
99 |  | 4610
100 |  |  | PLAN
101
102 |  | All distribution rebars = | 8 | 250
103
104
105 | [5 empty] | 175
106
107
108 |  |  | SECTION
109
110 | Provided rebars on drawings may be the same or greater than the above design requirements.
111
112
113
114
115

## S4 (hidden)
Slab-S2
CALCULATION OF B.M IN SLAB
|  |  |  | 0.078 |  | 0.102 | Wl2
0.046
[5 empty] | 0.078 | *Wl2
| l = | 2.425 | M
|  |  |  | w | = | 1.2 | t/sqm
Moment at ist Support |  |  | = | 0.71979 | t-m/m
Moment at 1st Span |  |  | = | 0.55043 | t-m/m
Moment at int Support |  |  | = | 0.55043 | t-m/m
Moment at int Span |  |  | = | 0.32461 | t-m/m
|  | Depth of slab | = | 150 | mm
|  | Effective Depth | = | 125 | mm
|  | Yield Stress of Reinf |  | 500 | n/mm2
Reinf as per Table-3,Pg-49,SP-16
| Reqd. reinf | Mu/bd2 | ptxd/10 |  | Reqd |  | %of Reinf
For -ve moment i.e. top reinf. 1st supp |  | 0.691 | 0.186 | (0.186*1000*125)/100) | 232.5 | cm2/m | 0.186
For +ve moment 1st span |  | 0.52841 | 0.142 | (0.142*1000*)/100) | 177.5 | cm2/m | 0.142
For -ve moment i.e. top reinf. int supp |  | 0.52841 | 0.142 | (0.142*1000*)/100) | 177.5 | cm2/m | 0.142
For +ve moment int span |  | 0.31163 | 0.12 | (0.12*1000*)/100) | 150 | cm2/m | 0.12
| Main Reinforcements | F | spacing
For -ve moment i.e. top reinf. 1st supp |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | FALSE
For +ve moment 1st span |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
For -ve moment i.e. top reinf. int supp |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
For +ve moment intspan |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
0.16091
C. DEFLECTION CHECK
| Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
|  |  |  | Cantilever | 7
|  |  |  | Simply supported | 20
|  |  |  | Continuous | 26
| fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 335.21
| Multiplication factor corresponding to steel service stress of 0.161% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 1.2369
| Modified applicable ratio assuming 'Discontinuous' |  |  | = 26*1.24 = | 32.1584
| Actual 'Span' to 'Depth' ratio |  |  | = 2425/125 = | 19.4
OK from deflection considerations.

## S6 (hidden)
Slab-S6
CALCULATION OF B.M IN SLAB
|  |  |  | 0.078 |  | 0.102 | Wl2
0.046
[5 empty] | 0.078 | *Wl2
| l = | 1.5 | M
|  |  |  | w | = | 1.2 | t/sqm
Moment at ist Support |  |  | = | 0.2754 | t-m/m
Moment at 1st Span |  |  | = | 0.2106 | t-m/m
Moment at int Support |  |  | = | 0.2106 | t-m/m
Moment at int Span |  |  | = | 0.1242 | t-m/m
|  | Depth of slab | = | 150 | mm
|  | Effective Depth | = | 125 | mm
|  | Yield Stress of Reinf |  | 500 | n/mm2
Reinf as per Table-3,Pg-49,SP-16
| Reqd. reinf | Mu/bd2 | ptxd/10 |  | Reqd |  | %of Reinf
For -ve moment i.e. top reinf. 1st supp |  | 0.26438 | 0.12 | (0.12*1000*125)/100) | 150 | cm2/m | 0.12
For +ve moment 1st span |  | 0.20218 | 0.12 | (0.12*1000*)/100) | 150 | cm2/m | 0.12
For -ve moment i.e. top reinf. int supp |  | 0.20218 | 0.12 | (0.12*1000*)/100) | 150 | cm2/m | 0.12
For +ve moment int span |  | 0.11923 | 0.12 | (0.12*1000*)/100) | 150 | cm2/m | 0.12
| Main Reinforcements | F | spacing
For -ve moment i.e. top reinf. 1st supp |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
For +ve moment 1st span |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
For -ve moment i.e. top reinf. int supp |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
For +ve moment intspan |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
0.16091
C. DEFLECTION CHECK
| Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
|  |  |  | Cantilever | 7
|  |  |  | Simply supported | 20 | 2
|  |  |  | Continuous | 26
| fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 216.264
| Multiplication factor corresponding to steel service stress of 0.161% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 2
| Modified applicable ratio assuming 'Discontinuous' |  |  | = 26*2 = | 52
| Actual 'Span' to 'Depth' ratio |  |  | = 1500/125 = | 12
OK from deflection considerations.

## S7 (hidden)
STRUCTURE : |  | ADMIN BUILDING
ITEM : |  | SLAB, S7 | [5 empty] | 1 | 1 Interior panel
Sl. No. | ITEM | NOTN. | FORMULA | CALCULATIONS | VALUE | UNIT | REMARKS | 2 | 2 one short edge disc.
[8 empty] | 3 | 3 one long edge disc.
A | B | C | D | E | F | G | H | 4 | 4 Two adjacent edge disc.
A: 1; B: Longer clear span; D: =; F: 3955 | 5 | 5 Two short edge disc.
[8 empty] | 6 | 6 Two long. edge disc.
A: 2; B: Sorter clear span; D: =; F: 2935 | 7 | 7 Three edge disc.(one Long edge cont.)
[8 empty] | 8 | 8 Three edge disc.(one short edge cont.)
A: 3; B: Thickness of Slab; D: =; F: 150 | 9 | 9 Four edge disc.
[10 empty] | 1 | 1 | Interior panel
A: 4; B: Total UDL.; D: =; F: 1.2 |  |  | 2 | 2 | one short edge disc.
[10 empty] | 3 | 3 | one long edge disc.
A: 5; B: Support Condition; D: =; F: 2 one short edge disc. |  |  | 4 | 4 | Two adjacent edge disc.
[10 empty] | 5 | 5 | Two short edge disc.
A: 8; B: A. DESIGN FORCES |  |  | 7 | 7 | Three edge disc.(one Long edge cont.)
9 | Longer clear span |  |  |  | 3955 | <mm; m> | 3.955 |  |  | 7 | 7 | Three edge disc.(one short edge cont.)
10 | Sorter clear span |  |  |  | 2935 | <mm; m> | 2.935 |  |  | 8 | 8 | Four edge disc.
11
12 | Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 150 | <mm; m> | 0.15
| Clear cover to main reinf |  |  |  | 25 | mm
| Maximum diameter of bar |  |  |  | 10 | mm
| Facor of safety |  |  |  | 1.5 | mm
| minimum slab thkness |  |  |  | 110 | mm
| Permissible Mu/bd2 |  |  |  | 2.76
13 |  | OK,More than the min. as per tender.
14 |  | OK, From max. Mu/bd2 considerations as detailed hereunder.
15 |  | OK from deflection considerations as checked hereunder.
16 | The least effective depth in shorter / longer direction |  |  | = 150-25 -10/2 = | 120 | <mm; cm> | 12
17
| Total design UDL |  |  |  | 1.2 | t/m2
19 |  |  |  | Say | 1.2 | t/m2
21
22 | Longer effective span | LY |  | = 3955+120 = | 4075 | <mm; m> | 4.075
23 | Sorter effective span | Lx |  | = 2935+120 = | 3055 | <mm; m> | 3.055
24 |  |  | Ly/Lx | = 4075/3055 = | 1.33
26
27 | Shorter of the two spans (for use in bending moment calculations) |  |  |  | 3055 | <mm; m> | 3.055
28
29 | Refering IS-456, Table-22, P91 |  | 2 | 2 one short edge disc.
30 | -ve support moment at continuous edge across long span | -My | 0.0522 | = 0.052*1.2*3.06^2 = | 0.58462 | tm
31 | +ve moment at mid span across long span | +My | 0.0396 | = 0.04*1.2*3.06^2 = | 0.44351 | tm
32 | -ve support moment at continuous edge across short span | -Mx | 0.037 | = 0.037*1.2*3.06^2 = | 0.41439 | tm
33 | +ve moment at mid span across short span | +Mx | 0.028 | = 0.028*1.2*3.06^2 = | 0.31359 | tm
34
35 | B. REINFORCEMENTS
36 | -ve Mu/bd2 at support across long span |  | = 1.5*0.58*10000/120^2 = |  | 0.60898 | N/mm2
37 | +ve Mu/bd2 at mid span across long span |  | = 1.5*0.44*10000/120^2 = |  | 0.46198 | N/mm2
38 | -ve Mu/bd2 at support across short span |  | = 1.5*0.41*10000/120^2 = |  | 0.43165 | N/mm2
39 | +ve Mu/bd2 at mid span across short span |  | = 1.5*0.31*10000/120^2 = |  | 0.32666 | N/mm2
40
41 | Max. Mu/bd2 |  |  | Max. of (0.61:0.33) | 0.60898 | N/mm2
44 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
45 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
46
47 |  |  | Reinf as per Table-2,Pg-48,SP-16
48 | Reqd. reinf | Mu/bd2 | ptxd/10
49
50 | For -ve moment i.e. top reinf. across long span | 0.60898 | 0.142 | = 0.142*12/10 = | 1.704 | cm2/m
51 | For +ve moment i.e. bottom reinf. across long span | 0.46198 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
52 | For -ve moment i.e. top reinf. across short span | 0.43165 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
53 | For +ve moment i.e. bottom reinf. across short span | 0.32666 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
54
55 | Main Reinforcements | F | spacing
56 | At top across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
57 | At bottom across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
58 | At top across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
59 | At bottom across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
60 |  |  |  |  | Max. % steel = |  | 0.168
62 | Max. permissible spacing | 3 | 360 | (As per Cl. 26.3.3; Pg. 46; IS:456)
63 |  | or | 300
64 | Least of the two |  | 300
65 | Max. provided spacing |  | 250
66 |  |  | OK
68 | Distribution Reinforcement
69 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
70 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
71 | Provide | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m
72 | Max. permissible spacing | 5 | 600 | (As per Cl. 26.3.3; Pg. 46; IS:456)
73 |  | or | 450
74 | Least of the two |  | 450
75 | Max. provided spacing |  | 250
76 |  |  | OK
78 | C. DEFLECTION CHECK
79 | Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
80 |  |  |  | Cantilever | 7
81 |  |  |  | Simply supported | 20
82 |  |  |  | Continuous | 26
83 | fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 245.6761
| Multiplication factor corresponding to steel service stress of 0.168% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 1.8801
84 | Modified applicable ratio assuming 'Discontinuous' |  |  | = 1.88*26 = | 48.8818
85 | Actual 'Span' to 'Depth' ratio |  |  | = 2935/120 = | 24.4583
86 |  | OK from deflection considerations.
87
88 | D. SKETCH
89
90 |  |  |  | 8 | 250
91
92 |  |  | 8 | 250
93
94 | 2935
95 |  |  |  |  | 8 | 250
96 |  |  | 8 | 250
97
98
99 |  | 3955
100 |  |  | PLAN
101
102 |  | All distribution rebars = | 8 | 250
103
104
105 | [5 empty] | 150
106
107
108 |  |  | SECTION
109
110 | Provided rebars on drawings may be the same or greater than the above design requirements.
111
112
113
114
115

## S8 (hidden)
STRUCTURE : |  | ADMIN BUILDING
ITEM : |  | SLAB, S8 | [5 empty] | 1 | 1 Interior panel
Sl. No. | ITEM | NOTN. | FORMULA | CALCULATIONS | VALUE | UNIT | REMARKS | 2 | 2 one short edge disc.
[8 empty] | 3 | 3 one long edge disc.
A | B | C | D | E | F | G | H | 4 | 4 Two adjacent edge disc.
A: 1; B: Longer clear span; D: =; F: 3505 | 5 | 5 Two short edge disc.
[8 empty] | 6 | 6 Two long. edge disc.
A: 2; B: Sorter clear span; D: =; F: 3420 | 7 | 7 Three edge disc.(one Long edge cont.)
[8 empty] | 8 | 8 Three edge disc.(one short edge cont.)
A: 3; B: Thickness of Slab; D: =; F: 150 | 9 | 9 Four edge disc.
[10 empty] | 1 | 1 | Interior panel
A: 4; B: Total UDL.; D: =; F: 1.2 |  |  | 2 | 2 | one short edge disc.
[10 empty] | 3 | 3 | one long edge disc.
A: 5; B: Support Condition; D: =; F: 2 one short edge disc. |  |  | 4 | 4 | Two adjacent edge disc.
[10 empty] | 5 | 5 | Two short edge disc.
A: 8; B: A. DESIGN FORCES |  |  | 7 | 7 | Three edge disc.(one Long edge cont.)
9 | Longer clear span |  |  |  | 3505 | <mm; m> | 3.505 |  |  | 7 | 7 | Three edge disc.(one short edge cont.)
10 | Sorter clear span |  |  |  | 3420 | <mm; m> | 3.42 |  |  | 8 | 8 | Four edge disc.
11
12 | Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 150 | <mm; m> | 0.15
| Clear cover to main reinf |  |  |  | 25 | mm
| Maximum diameter of bar |  |  |  | 10 | mm
| Facor of safety |  |  |  | 1.5 | mm
| minimum slab thkness |  |  |  | 110 | mm
| Permissible Mu/bd2 |  |  |  | 2.76
13 |  | OK,More than the min. as per tender.
14 |  | OK, From max. Mu/bd2 considerations as detailed hereunder.
15 |  | OK from deflection considerations as checked hereunder.
16 | The least effective depth in shorter / longer direction |  |  | = 150-25 -10/2 = | 120 | <mm; cm> | 12
17
| Total design UDL |  |  |  | 1.2 | t/m2
19 |  |  |  | Say | 1.2 | t/m2
21
22 | Longer effective span | LY |  | = 3505+120 = | 3625 | <mm; m> | 3.625
23 | Sorter effective span | Lx |  | = 3420+120 = | 3540 | <mm; m> | 3.54
24 |  |  | Ly/Lx | = 3625/3540 = | 1.02
26
27 | Shorter of the two spans (for use in bending moment calculations) |  |  |  | 3540 | <mm; m> | 3.54
28
29 | Refering IS-456, Table-22, P91 |  | 2 | 2 one short edge disc.
30 | -ve support moment at continuous edge across long span | -My | 0.0382 | = 0.038*1.2*3.54^2 = | 0.57445 | tm
31 | +ve moment at mid span across long span | +My | 0.0288 | = 0.029*1.2*3.54^2 = | 0.43309 | tm
32 | -ve support moment at continuous edge across short span | -Mx | 0.037 | = 0.037*1.2*3.54^2 = | 0.5564 | tm
33 | +ve moment at mid span across short span | +Mx | 0.028 | = 0.028*1.2*3.54^2 = | 0.42106 | tm
34
35 | B. REINFORCEMENTS
36 | -ve Mu/bd2 at support across long span |  | = 1.5*0.57*10000/120^2 = |  | 0.59838 | N/mm2
37 | +ve Mu/bd2 at mid span across long span |  | = 1.5*0.43*10000/120^2 = |  | 0.45114 | N/mm2
38 | -ve Mu/bd2 at support across short span |  | = 1.5*0.56*10000/120^2 = |  | 0.57959 | N/mm2
39 | +ve Mu/bd2 at mid span across short span |  | = 1.5*0.42*10000/120^2 = |  | 0.43861 | N/mm2
40
41 | Max. Mu/bd2 |  |  | Max. of (0.6:0.44) | 0.59838 | N/mm2
44 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
45 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
46
47 |  |  | Reinf as per Table-2,Pg-48,SP-16
48 | Reqd. reinf | Mu/bd2 | ptxd/10
49
50 | For -ve moment i.e. top reinf. across long span | 0.59838 | 0.1396 | = 0.14*12/10 = | 1.6752 | cm2/m
51 | For +ve moment i.e. bottom reinf. across long span | 0.45114 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
52 | For -ve moment i.e. top reinf. across short span | 0.57959 | 0.1348 | = 0.135*12/10 = | 1.6176 | cm2/m
53 | For +ve moment i.e. bottom reinf. across short span | 0.43861 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
54
55 | Main Reinforcements | F | spacing
56 | At top across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
57 | At bottom across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
58 | At top across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
59 | At bottom across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
60 |  |  |  |  | Max. % steel = |  | 0.168
62 | Max. permissible spacing | 3 | 360 | (As per Cl. 26.3.3; Pg. 46; IS:456)
63 |  | or | 300
64 | Least of the two |  | 300
65 | Max. provided spacing |  | 250
66 |  |  | OK
68 | Distribution Reinforcement
69 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
70 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
71 | Provide | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m
72 | Max. permissible spacing | 5 | 600 | (As per Cl. 26.3.3; Pg. 46; IS:456)
73 |  | or | 450
74 | Least of the two |  | 450
75 | Max. provided spacing |  | 250
76 |  |  | OK
78 | C. DEFLECTION CHECK
79 | Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
80 |  |  |  | Cantilever | 7
81 |  |  |  | Simply supported | 20
82 |  |  |  | Continuous | 26
83 | fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 241.5239
| Multiplication factor corresponding to steel service stress of 0.168% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 1.9285
84 | Modified applicable ratio assuming 'Discontinuous' |  |  | = 1.93*26 = | 50.1422
85 | Actual 'Span' to 'Depth' ratio |  |  | = 3420/120 = | 28.5
86 |  | OK from deflection considerations.
87
88 | D. SKETCH
89
90 |  |  |  | 8 | 250
91
92 |  |  | 8 | 250
93
94 | 3420
95 |  |  |  |  | 8 | 250
96 |  |  | 8 | 250
97
98
99 |  | 3505
100 |  |  | PLAN
101
102 |  | All distribution rebars = | 8 | 250
103
104
105 | [5 empty] | 150
106
107
108 |  |  | SECTION
109
110 | Provided rebars on drawings may be the same or greater than the above design requirements.
111
112
113
114
115

## S9 (hidden)
STRUCTURE : |  | ADMIN BUILDING
ITEM : |  | SLAB, S9 | [5 empty] | 1 | 1 Interior panel
Sl. No. | ITEM | NOTN. | FORMULA | CALCULATIONS | VALUE | UNIT | REMARKS | 2 | 2 one short edge disc.
[8 empty] | 3 | 3 one long edge disc.
A | B | C | D | E | F | G | H | 4 | 4 Two adjacent edge disc.
A: 1; B: Longer clear span; D: =; F: 3420 | 5 | 5 Two short edge disc.
[8 empty] | 6 | 6 Two long. edge disc.
A: 2; B: Sorter clear span; D: =; F: 2760 | 7 | 7 Three edge disc.(one Long edge cont.)
[8 empty] | 8 | 8 Three edge disc.(one short edge cont.)
A: 3; B: Thickness of Slab; D: =; F: 150 | 9 | 9 Four edge disc.
[10 empty] | 1 | 1 | Interior panel
A: 4; B: Total UDL.; D: =; F: 1.2 |  |  | 2 | 2 | one short edge disc.
[10 empty] | 3 | 3 | one long edge disc.
A: 5; B: Support Condition; D: =; F: 1 Interior panel |  |  | 4 | 4 | Two adjacent edge disc.
[10 empty] | 5 | 5 | Two short edge disc.
A: 8; B: A. DESIGN FORCES |  |  | 7 | 7 | Three edge disc.(one Long edge cont.)
9 | Longer clear span |  |  |  | 3420 | <mm; m> | 3.42 |  |  | 7 | 7 | Three edge disc.(one short edge cont.)
10 | Sorter clear span |  |  |  | 2760 | <mm; m> | 2.76 |  |  | 8 | 8 | Four edge disc.
11
12 | Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 150 | <mm; m> | 0.15
| Clear cover to main reinf |  |  |  | 25 | mm
| Maximum diameter of bar |  |  |  | 10 | mm
| Facor of safety |  |  |  | 1.5 | mm
| minimum slab thkness |  |  |  | 110 | mm
| Permissible Mu/bd2 |  |  |  | 2.76
13 |  | OK,More than the min. as per tender.
14 |  | OK, From max. Mu/bd2 considerations as detailed hereunder.
15 |  | OK from deflection considerations as checked hereunder.
16 | The least effective depth in shorter / longer direction |  |  | = 150-25 -10/2 = | 120 | <mm; cm> | 12
17
| Total design UDL |  |  |  | 1.2 | t/m2
19 |  |  |  | Say | 1.2 | t/m2
21
22 | Longer effective span | LY |  | = 3420+120 = | 3540 | <mm; m> | 3.54
23 | Sorter effective span | Lx |  | = 2760+120 = | 2880 | <mm; m> | 2.88
24 |  |  | Ly/Lx | = 3540/2880 = | 1.23
26
27 | Shorter of the two spans (for use in bending moment calculations) |  |  |  | 2880 | <mm; m> | 2.88
28
29 | Refering IS-456, Table-22, P91 |  | 1 | 1 Interior panel
30 | -ve support moment at continuous edge across long span | -My | 0.0442 | = 0.044*1.2*2.88^2 = | 0.43993 | tm
31 | +ve moment at mid span across long span | +My | 0.0332 | = 0.033*1.2*2.88^2 = | 0.33045 | tm
32 | -ve support moment at continuous edge across short span | -Mx | 0.032 | = 0.032*1.2*2.88^2 = | 0.3185 | tm
33 | +ve moment at mid span across short span | +Mx | 0.024 | = 0.024*1.2*2.88^2 = | 0.23888 | tm
34
35 | B. REINFORCEMENTS
36 | -ve Mu/bd2 at support across long span |  | = 1.5*0.44*10000/120^2 = |  | 0.45827 | N/mm2
37 | +ve Mu/bd2 at mid span across long span |  | = 1.5*0.33*10000/120^2 = |  | 0.34422 | N/mm2
38 | -ve Mu/bd2 at support across short span |  | = 1.5*0.32*10000/120^2 = |  | 0.33178 | N/mm2
39 | +ve Mu/bd2 at mid span across short span |  | = 1.5*0.24*10000/120^2 = |  | 0.24883 | N/mm2
40
41 | Max. Mu/bd2 |  |  | Max. of (0.46:0.25) | 0.45827 | N/mm2
44 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
45 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
46
47 |  |  | Reinf as per Table-2,Pg-48,SP-16
48 | Reqd. reinf | Mu/bd2 | ptxd/10
49
50 | For -ve moment i.e. top reinf. across long span | 0.45827 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
51 | For +ve moment i.e. bottom reinf. across long span | 0.34422 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
52 | For -ve moment i.e. top reinf. across short span | 0.33178 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
53 | For +ve moment i.e. bottom reinf. across short span | 0.24883 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
54
55 | Main Reinforcements | F | spacing
56 | At top across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
57 | At bottom across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
58 | At top across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
59 | At bottom across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
60 |  |  |  |  | Max. % steel = |  | 0.168
62 | Max. permissible spacing | 3 | 360 | (As per Cl. 26.3.3; Pg. 46; IS:456)
63 |  | or | 300
64 | Least of the two |  | 300
65 | Max. provided spacing |  | 250
66 |  |  | OK
68 | Distribution Reinforcement
69 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
70 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
71 | Provide | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m
72 | Max. permissible spacing | 5 | 600 | (As per Cl. 26.3.3; Pg. 46; IS:456)
73 |  | or | 450
74 | Least of the two |  | 450
75 | Max. provided spacing |  | 250
76 |  |  | OK
78 | C. DEFLECTION CHECK
79 | Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
80 |  |  |  | Cantilever | 7
81 |  |  |  | Simply supported | 20
82 |  |  |  | Continuous | 26
83 | fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 207.6136
| Multiplication factor corresponding to steel service stress of 0.168% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 2
84 | Modified applicable ratio assuming 'Discontinuous' |  |  | = 2*26 = | 52
85 | Actual 'Span' to 'Depth' ratio |  |  | = 2760/120 = | 23
86 |  | OK from deflection considerations.
87
88 | D. SKETCH
89
90 |  |  |  | 8 | 250
91
92 |  |  | 8 | 250
93
94 | 2760
95 |  |  |  |  | 8 | 250
96 |  |  | 8 | 250
97
98
99 |  | 3420
100 |  |  | PLAN
101
102 |  | All distribution rebars = | 8 | 250
103
104
105 | [5 empty] | 150
106
107
108 |  |  | SECTION
109
110 | Provided rebars on drawings may be the same or greater than the above design requirements.
111
112
113
114
115

## S10 (hidden)
STRUCTURE : |  | ADMIN BUILDING
ITEM : |  | SLAB, S10 | [5 empty] | 1 | 1 Interior panel
Sl. No. | ITEM | NOTN. | FORMULA | CALCULATIONS | VALUE | UNIT | REMARKS | 2 | 2 one short edge disc.
[8 empty] | 3 | 3 one long edge disc.
A | B | C | D | E | F | G | H | 4 | 4 Two adjacent edge disc.
A: 1; B: Longer clear span; D: =; F: 2305 | 5 | 5 Two short edge disc.
[8 empty] | 6 | 6 Two long. edge disc.
A: 2; B: Sorter clear span; D: =; F: 1635 | 7 | 7 Three edge disc.(one Long edge cont.)
[8 empty] | 8 | 8 Three edge disc.(one short edge cont.)
A: 3; B: Thickness of Slab; D: =; F: 150 | 9 | 9 Four edge disc.
[10 empty] | 1 | 1 | Interior panel
A: 4; B: Total UDL.; D: =; F: 1.35 |  |  | 2 | 2 | one short edge disc.
[10 empty] | 3 | 3 | one long edge disc.
A: 5; B: Support Condition; D: =; F: 4 Two adjacent edge disc. |  |  | 4 | 4 | Two adjacent edge disc.
[10 empty] | 5 | 5 | Two short edge disc.
A: 8; B: A. DESIGN FORCES |  |  | 7 | 7 | Three edge disc.(one Long edge cont.)
9 | Longer clear span |  |  |  | 2305 | <mm; m> | 2.305 |  |  | 7 | 7 | Three edge disc.(one short edge cont.)
10 | Sorter clear span |  |  |  | 1635 | <mm; m> | 1.635 |  |  | 8 | 8 | Four edge disc.
11
12 | Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 150 | <mm; m> | 0.15
| Clear cover to main reinf |  |  |  | 25 | mm
| Maximum diameter of bar |  |  |  | 10 | mm
| Facor of safety |  |  |  | 1.5 | mm
| minimum slab thkness |  |  |  | 110 | mm
| Permissible Mu/bd2 |  |  |  | 2.76
13 |  | OK,More than the min. as per tender.
14 |  | OK, From max. Mu/bd2 considerations as detailed hereunder.
15 |  | OK from deflection considerations as checked hereunder.
16 | The least effective depth in shorter / longer direction |  |  | = 150-25 -10/2 = | 120 | <mm; cm> | 12
17
| Total design UDL |  |  |  | 1.35 | t/m2
19 |  |  |  | Say | 1.35 | t/m2
21
22 | Longer effective span | LY |  | = 2305+120 = | 2425 | <mm; m> | 2.425
23 | Sorter effective span | Lx |  | = 1635+120 = | 1755 | <mm; m> | 1.755
24 |  |  | Ly/Lx | = 2425/1755 = | 1.38
26
27 | Shorter of the two spans (for use in bending moment calculations) |  |  |  | 1755 | <mm; m> | 1.755
28
29 | Refering IS-456, Table-22, P91 |  | 4 | 4 Two adjacent edge disc.
30 | -ve support moment at continuous edge across long span | -My | 0.0698 | = 0.07*1.35*1.76^2 = | 0.29023 | tm
31 | +ve moment at mid span across long span | +My | 0.0522 | = 0.052*1.35*1.76^2 = | 0.21705 | tm
32 | -ve support moment at continuous edge across short span | -Mx | 0.047 | = 0.047*1.35*1.76^2 = | 0.19543 | tm
33 | +ve moment at mid span across short span | +Mx | 0.035 | = 0.035*1.35*1.76^2 = | 0.14553 | tm
34
35 | B. REINFORCEMENTS
36 | -ve Mu/bd2 at support across long span |  | = 1.5*0.29*10000/120^2 = |  | 0.30232 | N/mm2
37 | +ve Mu/bd2 at mid span across long span |  | = 1.5*0.22*10000/120^2 = |  | 0.22609 | N/mm2
38 | -ve Mu/bd2 at support across short span |  | = 1.5*0.2*10000/120^2 = |  | 0.20357 | N/mm2
39 | +ve Mu/bd2 at mid span across short span |  | = 1.5*0.15*10000/120^2 = |  | 0.15159 | N/mm2
40
41 | Max. Mu/bd2 |  |  | Max. of (0.3:0.15) | 0.30232 | N/mm2
44 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
45 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
46
47 |  |  | Reinf as per Table-2,Pg-48,SP-16
48 | Reqd. reinf | Mu/bd2 | ptxd/10
49
50 | For -ve moment i.e. top reinf. across long span | 0.30232 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
51 | For +ve moment i.e. bottom reinf. across long span | 0.22609 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
52 | For -ve moment i.e. top reinf. across short span | 0.20357 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
53 | For +ve moment i.e. bottom reinf. across short span | 0.15159 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
54
55 | Main Reinforcements | F | spacing
56 | At top across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
57 | At bottom across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
58 | At top across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
59 | At bottom across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
60 |  |  |  |  | Max. % steel = |  | 0.168
62 | Max. permissible spacing | 3 | 360 | (As per Cl. 26.3.3; Pg. 46; IS:456)
63 |  | or | 300
64 | Least of the two |  | 300
65 | Max. provided spacing |  | 250
66 |  |  | OK
68 | Distribution Reinforcement
69 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
70 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
71 | Provide | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m
72 | Max. permissible spacing | 5 | 600 | (As per Cl. 26.3.3; Pg. 46; IS:456)
73 |  | or | 450
74 | Least of the two |  | 450
75 | Max. provided spacing |  | 250
76 |  |  | OK
78 | C. DEFLECTION CHECK
79 | Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
80 |  |  |  | Cantilever | 7
81 |  |  |  | Simply supported | 20
82 |  |  |  | Continuous | 26
83 | fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 207.6136
| Multiplication factor corresponding to steel service stress of 0.168% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 2
84 | Modified applicable ratio assuming 'Discontinuous' |  |  | = 2*26 = | 52
85 | Actual 'Span' to 'Depth' ratio |  |  | = 1635/120 = | 13.625
86 |  | OK from deflection considerations.
87
88 | D. SKETCH
89
90 |  |  |  | 8 | 250
91
92 |  |  | 8 | 250
93
94 | 1635
95 |  |  |  |  | 8 | 250
96 |  |  | 8 | 250
97
98
99 |  | 2305
100 |  |  | PLAN
101
102 |  | All distribution rebars = | 8 | 250
103
104
105 | [5 empty] | 150
106
107
108 |  |  | SECTION
109
110 | Provided rebars on drawings may be the same or greater than the above design requirements.
111
112
113
114
115

## S11 (hidden)
Slab-S11
CALCULATION OF B.M IN SLAB
|  |  |  | 0.078 |  | 0.102 | Wl2
0.046
[5 empty] | 0.078 | *Wl2
| l = | 1.41 | M
|  |  |  | w | = | 1.35 | t/sqm
Moment at ist Support |  |  | = | 0.27376 | t-m/m
Moment at 1st Span |  |  | = | 0.20935 | t-m/m
Moment at int Support |  |  | = | 0.20935 | t-m/m
Moment at int Span |  |  | = | 0.12346 | t-m/m
|  | Depth of slab | = | 150 | mm
|  | Effective Depth | = | 125 | mm
|  | Yield Stress of Reinf |  | 500 | n/mm2
Reinf as per Table-3,Pg-49,SP-16
| Reqd. reinf | Mu/bd2 | ptxd/10 |  | Reqd |  | %of Reinf
For -ve moment i.e. top reinf. 1st supp |  | 0.26281 | 0.12 | (0.12*1000*125)/100) | 150 | cm2/m | 0.12
For +ve moment 1st span |  | 0.20097 | 0.12 | (0.12*1000*)/100) | 150 | cm2/m | 0.12
For -ve moment i.e. top reinf. int supp |  | 0.20097 | 0.12 | (0.12*1000*)/100) | 150 | cm2/m | 0.12
For +ve moment int span |  | 0.11852 | 0.12 | (0.12*1000*)/100) | 150 | cm2/m | 0.12
| Main Reinforcements | F | spacing
For -ve moment i.e. top reinf. 1st supp |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
For +ve moment 1st span |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
For -ve moment i.e. top reinf. int supp |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
For +ve moment intspan |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
0.16091
C. DEFLECTION CHECK
| Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
|  |  |  | Cantilever | 7
|  |  |  | Simply supported | 20
|  |  |  | Continuous | 26
| fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 216.264
| Multiplication factor corresponding to steel service stress of 0.161% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 2
| Modified applicable ratio assuming 'Discontinuous' |  |  | = 26*2 = | 52
| Actual 'Span' to 'Depth' ratio |  |  | = 1410/125 = | 11.28
OK from deflection considerations.

## S12 (hidden)
STRUCTURE : |  | ADMIN BUILDING
ITEM : |  | SLAB, S12 | [5 empty] | 1 | 1 Interior panel
Sl. No. | ITEM | NOTN. | FORMULA | CALCULATIONS | VALUE | UNIT | REMARKS | 2 | 2 one short edge disc.
[8 empty] | 3 | 3 one long edge disc.
A | B | C | D | E | F | G | H | 4 | 4 Two adjacent edge disc.
A: 1; B: Longer clear span; D: =; F: 2305 | 5 | 5 Two short edge disc.
[8 empty] | 6 | 6 Two long. edge disc.
A: 2; B: Sorter clear span; D: =; F: 1775 | 7 | 7 Three edge disc.(one Long edge cont.)
[8 empty] | 8 | 8 Three edge disc.(one short edge cont.)
A: 3; B: Thickness of Slab; D: =; F: 150 | 9 | 9 Four edge disc.
[10 empty] | 1 | 1 | Interior panel
A: 4; B: Total UDL.; D: =; F: 1.35 |  |  | 2 | 2 | one short edge disc.
[10 empty] | 3 | 3 | one long edge disc.
A: 5; B: Support Condition; D: =; F: 4 Two adjacent edge disc. |  |  | 4 | 4 | Two adjacent edge disc.
[10 empty] | 5 | 5 | Two short edge disc.
A: 8; B: A. DESIGN FORCES |  |  | 7 | 7 | Three edge disc.(one Long edge cont.)
9 | Longer clear span |  |  |  | 2305 | <mm; m> | 2.305 |  |  | 7 | 7 | Three edge disc.(one short edge cont.)
10 | Sorter clear span |  |  |  | 1775 | <mm; m> | 1.775 |  |  | 8 | 8 | Four edge disc.
11
12 | Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 150 | <mm; m> | 0.15
| Clear cover to main reinf |  |  |  | 25 | mm
| Maximum diameter of bar |  |  |  | 10 | mm
| Facor of safety |  |  |  | 1.5 | mm
| minimum slab thkness |  |  |  | 110 | mm
| Permissible Mu/bd2 |  |  |  | 2.76
13 |  | OK,More than the min. as per tender.
14 |  | OK, From max. Mu/bd2 considerations as detailed hereunder.
15 |  | OK from deflection considerations as checked hereunder.
16 | The least effective depth in shorter / longer direction |  |  | = 150-25 -10/2 = | 120 | <mm; cm> | 12
17
| Total design UDL |  |  |  | 1.35 | t/m2
19 |  |  |  | Say | 1.35 | t/m2
21
22 | Longer effective span | LY |  | = 2305+120 = | 2425 | <mm; m> | 2.425
23 | Sorter effective span | Lx |  | = 1775+120 = | 1895 | <mm; m> | 1.895
24 |  |  | Ly/Lx | = 2425/1895 = | 1.28
26
27 | Shorter of the two spans (for use in bending moment calculations) |  |  |  | 1895 | <mm; m> | 1.895
28
29 | Refering IS-456, Table-22, P91 |  | 4 | 4 Two adjacent edge disc.
30 | -ve support moment at continuous edge across long span | -My | 0.064 | = 0.064*1.35*1.9^2 = | 0.31026 | tm
31 | +ve moment at mid span across long span | +My | 0.0482 | = 0.048*1.35*1.9^2 = | 0.23367 | tm
32 | -ve support moment at continuous edge across short span | -Mx | 0.047 | = 0.047*1.35*1.9^2 = | 0.22785 | tm
33 | +ve moment at mid span across short span | +Mx | 0.035 | = 0.035*1.35*1.9^2 = | 0.16968 | tm
34
35 | B. REINFORCEMENTS
36 | -ve Mu/bd2 at support across long span |  | = 1.5*0.31*10000/120^2 = |  | 0.32319 | N/mm2
37 | +ve Mu/bd2 at mid span across long span |  | = 1.5*0.23*10000/120^2 = |  | 0.2434 | N/mm2
38 | -ve Mu/bd2 at support across short span |  | = 1.5*0.23*10000/120^2 = |  | 0.23734 | N/mm2
39 | +ve Mu/bd2 at mid span across short span |  | = 1.5*0.17*10000/120^2 = |  | 0.17675 | N/mm2
40
41 | Max. Mu/bd2 |  |  | Max. of (0.32:0.18) | 0.32319 | N/mm2
44 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
45 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
46
47 |  |  | Reinf as per Table-2,Pg-48,SP-16
48 | Reqd. reinf | Mu/bd2 | ptxd/10
49
50 | For -ve moment i.e. top reinf. across long span | 0.32319 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
51 | For +ve moment i.e. bottom reinf. across long span | 0.2434 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
52 | For -ve moment i.e. top reinf. across short span | 0.23734 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
53 | For +ve moment i.e. bottom reinf. across short span | 0.17675 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
54
55 | Main Reinforcements | F | spacing
56 | At top across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
57 | At bottom across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
58 | At top across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
59 | At bottom across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
60 |  |  |  |  | Max. % steel = |  | 0.168
62 | Max. permissible spacing | 3 | 360 | (As per Cl. 26.3.3; Pg. 46; IS:456)
63 |  | or | 300
64 | Least of the two |  | 300
65 | Max. provided spacing |  | 250
66 |  |  | OK
68 | Distribution Reinforcement
69 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
70 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
71 | Provide | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m
72 | Max. permissible spacing | 5 | 600 | (As per Cl. 26.3.3; Pg. 46; IS:456)
73 |  | or | 450
74 | Least of the two |  | 450
75 | Max. provided spacing |  | 250
76 |  |  | OK
78 | C. DEFLECTION CHECK
79 | Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
80 |  |  |  | Cantilever | 7
81 |  |  |  | Simply supported | 20
82 |  |  |  | Continuous | 26
83 | fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 207.6136
| Multiplication factor corresponding to steel service stress of 0.168% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 2
84 | Modified applicable ratio assuming 'Discontinuous' |  |  | = 2*26 = | 52
85 | Actual 'Span' to 'Depth' ratio |  |  | = 1775/120 = | 14.7917
86 |  | OK from deflection considerations.
87
88 | D. SKETCH
89
90 |  |  |  | 8 | 250
91
92 |  |  | 8 | 250
93
94 | 1775
95 |  |  |  |  | 8 | 250
96 |  |  | 8 | 250
97
98
99 |  | 2305
100 |  |  | PLAN
101
102 |  | All distribution rebars = | 8 | 250
103
104
105 | [5 empty] | 150
106
107
108 |  |  | SECTION
109
110 | Provided rebars on drawings may be the same or greater than the above design requirements.
111
112
113
114
115

## S13 (hidden)
Slab-S13
CALCULATION OF B.M IN SLAB
|  |  |  | 0.078 |  | 0.102 | Wl2
0.046
[5 empty] | 0.078 | *Wl2
| l = | 2.305 | M
|  |  |  | w | = | 1.35 | t/sqm
Moment at ist Support |  |  | = | 0.7316 | t-m/m
Moment at 1st Span |  |  | = | 0.55946 | t-m/m
Moment at int Support |  |  | = | 0.55946 | t-m/m
Moment at int Span |  |  | = | 0.32994 | t-m/m
|  | Depth of slab | = | 150 | mm
|  | Effective Depth | = | 125 | mm
|  | Yield Stress of Reinf |  | 500 | n/mm2
Reinf as per Table-3,Pg-49,SP-16
| Reqd. reinf | Mu/bd2 | ptxd/10 |  | Reqd |  | %of Reinf
For -ve moment i.e. top reinf. 1st supp |  | 0.70234 | 0.201 | (0.201*1000*125)/100) | 251.25 | cm2/m | 0.201
For +ve moment 1st span |  | 0.53708 | 0.142 | (0.142*1000*)/100) | 177.5 | cm2/m | 0.142
For -ve moment i.e. top reinf. int supp |  | 0.53708 | 0.142 | (0.142*1000*)/100) | 177.5 | cm2/m | 0.142
For +ve moment int span |  | 0.31674 | 0.12 | (0.12*1000*)/100) | 150 | cm2/m | 0.12
| Main Reinforcements | F | spacing
For -ve moment i.e. top reinf. 1st supp |  | 8 | 200 | = pi/4*(8/10)^2*1000/200 = | 251.4286 | cm2/m | 0.20114 | TRUE
For +ve moment 1st span |  | 8 | 200 | = pi/4*(8/10)^2*1000/200 = | 251.4286 | cm2/m | 0.20114 | TRUE
For -ve moment i.e. top reinf. int supp |  | 8 | 200 | = pi/4*(8/10)^2*1000/200 = | 251.4286 | cm2/m | 0.20114 | TRUE
For +ve moment intspan |  | 8 | 200 | = pi/4*(8/10)^2*1000/200 = | 251.4286 | cm2/m | 0.20114 | TRUE
0.20114
C. DEFLECTION CHECK
| Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
|  |  |  | Cantilever | 7
|  |  |  | Simply supported | 20
|  |  |  | Continuous | 26
| fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 289.794
| Multiplication factor corresponding to steel service stress of 0.201% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 1.3835
| Modified applicable ratio assuming 'Discontinuous' |  |  | = 26*1.38 = | 35.9699
| Actual 'Span' to 'Depth' ratio |  |  | = 2305/125 = | 18.44
OK from deflection considerations.

## S14 (hidden)
Slab-S14
CALCULATION OF B.M IN SLAB
|  |  |  | 0.078 |  | 0.102 | Wl2
0.046
[5 empty] | 0.078 | *Wl2
| l = | 1.41 | M
|  |  |  | w | = | 1.35 | t/sqm
Moment at ist Support |  |  | = | 0.27376 | t-m/m
Moment at 1st Span |  |  | = | 0.20935 | t-m/m
Moment at int Support |  |  | = | 0.20935 | t-m/m
Moment at int Span |  |  | = | 0.12346 | t-m/m
|  | Depth of slab | = | 150 | mm
|  | Effective Depth | = | 125 | mm
|  | Yield Stress of Reinf |  | 500 | n/mm2
Reinf as per Table-3,Pg-49,SP-16
| Reqd. reinf | Mu/bd2 | ptxd/10 |  | Reqd |  | %of Reinf
For -ve moment i.e. top reinf. 1st supp |  | 0.26281 | 0.12 | (0.12*1000*125)/100) | 150 | cm2/m | 0.12
For +ve moment 1st span |  | 0.20097 | 0.12 | (0.12*1000*)/100) | 150 | cm2/m | 0.12
For -ve moment i.e. top reinf. int supp |  | 0.20097 | 0.12 | (0.12*1000*)/100) | 150 | cm2/m | 0.12
For +ve moment int span |  | 0.11852 | 0.12 | (0.12*1000*)/100) | 150 | cm2/m | 0.12
| Main Reinforcements | F | spacing
For -ve moment i.e. top reinf. 1st supp |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
For +ve moment 1st span |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
For -ve moment i.e. top reinf. int supp |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
For +ve moment intspan |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
0.16091
C. DEFLECTION CHECK
| Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
|  |  |  | Cantilever | 7
|  |  |  | Simply supported | 20
|  |  |  | Continuous | 26
| fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 216.264
| Multiplication factor corresponding to steel service stress of 0.161% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 2
| Modified applicable ratio assuming 'Discontinuous' |  |  | = 26*2 = | 52
| Actual 'Span' to 'Depth' ratio |  |  | = 1410/125 = | 11.28
OK from deflection considerations.

## S15 (hidden)
STRUCTURE : |  | ADMIN BUILDING
ITEM : |  | SLAB, S15 | [5 empty] | 1 | 1 Interior panel
Sl. No. | ITEM | NOTN. | FORMULA | CALCULATIONS | VALUE | UNIT | REMARKS | 2 | 2 one short edge disc.
[8 empty] | 3 | 3 one long edge disc.
A | B | C | D | E | F | G | H | 4 | 4 Two adjacent edge disc.
A: 1; B: Longer clear span; D: =; F: 6535 | 5 | 5 Two short edge disc.
[8 empty] | 6 | 6 Two long. edge disc.
A: 2; B: Sorter clear span; D: =; F: 3830 | 7 | 7 Three edge disc.(one Long edge cont.)
[8 empty] | 8 | 8 Three edge disc.(one short edge cont.)
A: 3; B: Thickness of Slab; D: =; F: 150 | 9 | 9 Four edge disc.
[10 empty] | 1 | 1 | Interior panel
A: 4; B: Total UDL.; D: =; F: 1.2 |  |  | 2 | 2 | one short edge disc.
[10 empty] | 3 | 3 | one long edge disc.
A: 5; B: Support Condition; D: =; F: 8 Three edge disc.(one short edge cont.) |  |  | 4 | 4 | Two adjacent edge disc.
[10 empty] | 5 | 5 | Two short edge disc.
A: 8; B: A. DESIGN FORCES |  |  | 7 | 7 | Three edge disc.(one Long edge cont.)
9 | Longer clear span |  |  |  | 6535 | <mm; m> | 6.535 |  |  | 7 | 7 | Three edge disc.(one short edge cont.)
10 | Sorter clear span |  |  |  | 3830 | <mm; m> | 3.83 |  |  | 8 | 8 | Four edge disc.
11
12 | Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 150 | <mm; m> | 0.15
| Clear cover to main reinf |  |  |  | 25 | mm
| Maximum diameter of bar |  |  |  | 10 | mm
| Facor of safety |  |  |  | 1.5 | mm
| minimum slab thkness |  |  |  | 110 | mm
| Permissible Mu/bd2 |  |  |  | 2.76
13 |  | OK,More than the min. as per tender.
14 |  | OK, From max. Mu/bd2 considerations as detailed hereunder.
15 |  | OK from deflection considerations as checked hereunder.
16 | The least effective depth in shorter / longer direction |  |  | = 150-25 -10/2 = | 120 | <mm; cm> | 12
17
| Total design UDL |  |  |  | 1.2 | t/m2
19 |  |  |  | Say | 1.2 | t/m2
21
22 | Longer effective span | LY |  | = 6535+120 = | 6655 | <mm; m> | 6.655
23 | Sorter effective span | Lx |  | = 3830+120 = | 3950 | <mm; m> | 3.95
24 |  |  | Ly/Lx | = 6655/3950 = | 1.68
26
27 | Shorter of the two spans (for use in bending moment calculations) |  |  |  | 3950 | <mm; m> | 3.95
28
29 | Refering IS-456, Table-22, P91 |  | 8 | 8 Three edge disc.(one short edge cont.)
30 | -ve support moment at continuous edge across long span | -My | 0 | = 0*1.2*3.95^2 = | 0 | tm
31 | +ve moment at mid span across long span | +My | 0.08392 | = 0.084*1.2*3.95^2 = | 1.5712 | tm
32 | -ve support moment at continuous edge across short span | -Mx | 0.057 | = 0.057*1.2*3.95^2 = | 1.0672 | tm
33 | +ve moment at mid span across short span | +Mx | 0.043 | = 0.043*1.2*3.95^2 = | 0.80509 | tm
34
35 | B. REINFORCEMENTS
36 | -ve Mu/bd2 at support across long span |  | = 1.5*0*10000/120^2 = |  | 0 | N/mm2
37 | +ve Mu/bd2 at mid span across long span |  | = 1.5*1.57*10000/120^2 = |  | 1.6367 | N/mm2
38 | -ve Mu/bd2 at support across short span |  | = 1.5*1.07*10000/120^2 = |  | 1.1117 | N/mm2
39 | +ve Mu/bd2 at mid span across short span |  | = 1.5*0.81*10000/120^2 = |  | 0.83863 | N/mm2
40
41 | Max. Mu/bd2 |  |  | Max. of (0:0.84) | 1.6367 | N/mm2
44 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
45 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
46
47 |  |  | Reinf as per Table-2,Pg-48,SP-16
48 | Reqd. reinf | Mu/bd2 | ptxd/10
49
50 | For -ve moment i.e. top reinf. across long span | 0 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
51 | For +ve moment i.e. bottom reinf. across long span | 1.6367 | 0.4084 | = 0.408*12/10 = | 4.9008 | cm2/m
52 | For -ve moment i.e. top reinf. across short span | 1.1117 | 0.2696 | = 0.27*12/10 = | 3.2352 | cm2/m
53 | For +ve moment i.e. bottom reinf. across short span | 0.83863 | 0.1988 | = 0.199*12/10 = | 2.3856 | cm2/m
54
55 | Main Reinforcements | F | spacing
56 | At top across long span | 8 | 200 | = pi/4*(8/10)^2*1000/200 = | 2.5143 | cm2/m | 0.21
57 | At bottom across long span | 10 | 150 | = pi/4*(10/10)^2*1000/150 = | 5.2381 | cm2/m | 0.437
58 | At top across short span | 10 | 200 | = pi/4*(10/10)^2*1000/200 = | 3.9286 | cm2/m | 0.327
59 | At bottom across short span | 8 | 200 | = pi/4*(8/10)^2*1000/200 = | 2.5143 | cm2/m | 0.21
60 |  |  |  |  | Max. % steel = |  | 0.437
62 | Max. permissible spacing | 3 | 360 | (As per Cl. 26.3.3; Pg. 46; IS:456)
63 |  | or | 300
64 | Least of the two |  | 300
65 | Max. provided spacing |  | 200
66 |  |  | OK
68 | Distribution Reinforcement
69 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
70 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
71 | Provide | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m
72 | Max. permissible spacing | 5 | 600 | (As per Cl. 26.3.3; Pg. 46; IS:456)
73 |  | or | 450
74 | Least of the two |  | 450
75 | Max. provided spacing |  | 250
76 |  |  | OK
78 | C. DEFLECTION CHECK
79 | Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
80 |  |  |  | Cantilever | 7
81 |  |  |  | Simply supported | 20
82 |  |  |  | Continuous | 26
83 | fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 166.0909
| Multiplication factor corresponding to steel service stress of 0.437% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 1.8688
84 | Modified applicable ratio assuming 'Discontinuous' |  |  | = 1.87*26 = | 48.5878
85 | Actual 'Span' to 'Depth' ratio |  |  | = 3830/120 = | 31.9167
86 |  | OK from deflection considerations.
87
88 | D. SKETCH
89
90 |  |  |  | 8 | 200
91
92 |  |  | 10 | 150
93
94 | 3830
95 |  |  |  |  | 10 | 200
96 |  |  | 8 | 200
97
98
99 |  | 6535
100 |  |  | PLAN
101
102 |  | All distribution rebars = | 8 | 250
103
104
105 | [5 empty] | 150
106
107
108 |  |  | SECTION
109
110 | Provided rebars on drawings may be the same or greater than the above design requirements.
111
112
113
114
115

## S16 (hidden)
STRUCTURE : |  | ADMIN BUILDING
ITEM : |  | SLAB, S16 | [5 empty] | 1 | 1 Interior panel
Sl. No. | ITEM | NOTN. | FORMULA | CALCULATIONS | VALUE | UNIT | REMARKS | 2 | 2 one short edge disc.
[8 empty] | 3 | 3 one long edge disc.
A | B | C | D | E | F | G | H | 4 | 4 Two adjacent edge disc.
A: 1; B: Longer clear span; D: =; F: 4560 | 5 | 5 Two short edge disc.
[8 empty] | 6 | 6 Two long. edge disc.
A: 2; B: Sorter clear span; D: =; F: 3780 | 7 | 7 Three edge disc.(one Long edge cont.)
[8 empty] | 8 | 8 Three edge disc.(one short edge cont.)
A: 3; B: Thickness of Slab; D: =; F: 150 | 9 | 9 Four edge disc.
[10 empty] | 1 | 1 | Interior panel
A: 4; B: Total UDL.; D: =; F: 1.2 |  |  | 2 | 2 | one short edge disc.
[10 empty] | 3 | 3 | one long edge disc.
A: 5; B: Support Condition; D: =; F: 1 Interior panel |  |  | 4 | 4 | Two adjacent edge disc.
[10 empty] | 5 | 5 | Two short edge disc.
A: 8; B: A. DESIGN FORCES |  |  | 7 | 7 | Three edge disc.(one Long edge cont.)
9 | Longer clear span |  |  |  | 4560 | <mm; m> | 4.56 |  |  | 7 | 7 | Three edge disc.(one short edge cont.)
10 | Sorter clear span |  |  |  | 3780 | <mm; m> | 3.78 |  |  | 8 | 8 | Four edge disc.
11
12 | Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 150 | <mm; m> | 0.15
| Clear cover to main reinf |  |  |  | 25 | mm
| Maximum diameter of bar |  |  |  | 10 | mm
| Facor of safety |  |  |  | 1.5 | mm
| minimum slab thkness |  |  |  | 110 | mm
| Permissible Mu/bd2 |  |  |  | 2.76
13 |  | OK,More than the min. as per tender.
14 |  | OK, From max. Mu/bd2 considerations as detailed hereunder.
15 |  | OK from deflection considerations as checked hereunder.
16 | The least effective depth in shorter / longer direction |  |  | = 150-25 -10/2 = | 120 | <mm; cm> | 12
17
| Total design UDL |  |  |  | 1.2 | t/m2
19 |  |  |  | Say | 1.2 | t/m2
21
22 | Longer effective span | LY |  | = 4560+120 = | 4680 | <mm; m> | 4.68
23 | Sorter effective span | Lx |  | = 3780+120 = | 3900 | <mm; m> | 3.9
24 |  |  | Ly/Lx | = 4680/3900 = | 1.2
26
27 | Shorter of the two spans (for use in bending moment calculations) |  |  |  | 3900 | <mm; m> | 3.9
28
29 | Refering IS-456, Table-22, P91 |  | 1 | 1 Interior panel
30 | -ve support moment at continuous edge across long span | -My | 0.043 | = 0.043*1.2*3.9^2 = | 0.78484 | tm
31 | +ve moment at mid span across long span | +My | 0.032 | = 0.032*1.2*3.9^2 = | 0.58406 | tm
32 | -ve support moment at continuous edge across short span | -Mx | 0.032 | = 0.032*1.2*3.9^2 = | 0.58406 | tm
33 | +ve moment at mid span across short span | +Mx | 0.024 | = 0.024*1.2*3.9^2 = | 0.43805 | tm
34
35 | B. REINFORCEMENTS
36 | -ve Mu/bd2 at support across long span |  | = 1.5*0.78*10000/120^2 = |  | 0.81754 | N/mm2
37 | +ve Mu/bd2 at mid span across long span |  | = 1.5*0.58*10000/120^2 = |  | 0.6084 | N/mm2
38 | -ve Mu/bd2 at support across short span |  | = 1.5*0.58*10000/120^2 = |  | 0.6084 | N/mm2
39 | +ve Mu/bd2 at mid span across short span |  | = 1.5*0.44*10000/120^2 = |  | 0.4563 | N/mm2
40
41 | Max. Mu/bd2 |  |  | Max. of (0.82:0.46) | 0.81754 | N/mm2
44 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
45 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
46
47 |  |  | Reinf as per Table-2,Pg-48,SP-16
48 | Reqd. reinf | Mu/bd2 | ptxd/10
49
50 | For -ve moment i.e. top reinf. across long span | 0.81754 | 0.1936 | = 0.194*12/10 = | 2.3232 | cm2/m
51 | For +ve moment i.e. bottom reinf. across long span | 0.6084 | 0.142 | = 0.142*12/10 = | 1.704 | cm2/m
52 | For -ve moment i.e. top reinf. across short span | 0.6084 | 0.142 | = 0.142*12/10 = | 1.704 | cm2/m
53 | For +ve moment i.e. bottom reinf. across short span | 0.4563 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
54
55 | Main Reinforcements | F | spacing
56 | At top across long span | 8 | 200 | = pi/4*(8/10)^2*1000/200 = | 2.5143 | cm2/m | 0.21
57 | At bottom across long span | 8 | 200 | = pi/4*(8/10)^2*1000/200 = | 2.5143 | cm2/m | 0.21
58 | At top across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
59 | At bottom across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
60 |  |  |  |  | Max. % steel = |  | 0.21
62 | Max. permissible spacing | 3 | 360 | (As per Cl. 26.3.3; Pg. 46; IS:456)
63 |  | or | 300
64 | Least of the two |  | 300
65 | Max. provided spacing |  | 250
66 |  |  | OK
68 | Distribution Reinforcement
69 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
70 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
71 | Provide | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m
72 | Max. permissible spacing | 5 | 600 | (As per Cl. 26.3.3; Pg. 46; IS:456)
73 |  | or | 450
74 | Least of the two |  | 450
75 | Max. provided spacing |  | 250
76 |  |  | OK
78 | C. DEFLECTION CHECK
79 | Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
80 |  |  |  | Cantilever | 7
81 |  |  |  | Simply supported | 20
82 |  |  |  | Continuous | 26
83 | fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 267.96
| Multiplication factor corresponding to steel service stress of 0.21% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 1.5055
84 | Modified applicable ratio assuming 'Discontinuous' |  |  | = 1.51*26 = | 39.1438
85 | Actual 'Span' to 'Depth' ratio |  |  | = 3780/120 = | 31.5
86 |  | OK from deflection considerations.
87
88 | D. SKETCH
89
90 |  |  |  | 8 | 200
91
92 |  |  | 8 | 200
93
94 | 3780
95 |  |  |  |  | 8 | 250
96 |  |  | 8 | 250
97
98
99 |  | 4560
100 |  |  | PLAN
101
102 |  | All distribution rebars = | 8 | 250
103
104
105 | [5 empty] | 150
106
107
108 |  |  | SECTION
109
110 | Provided rebars on drawings may be the same or greater than the above design requirements.
111
112
113
114
115

## S17 (hidden)
STRUCTURE : |  | ADMIN BUILDING
ITEM : |  | SLAB, S17 | [5 empty] | 1 | 1 Interior panel
Sl. No. | ITEM | NOTN. | FORMULA | CALCULATIONS | VALUE | UNIT | REMARKS | 2 | 2 one short edge disc.
[8 empty] | 3 | 3 one long edge disc.
A | B | C | D | E | F | G | H | 4 | 4 Two adjacent edge disc.
A: 1; B: Longer clear span; D: =; F: 4235 | 5 | 5 Two short edge disc.
[8 empty] | 6 | 6 Two long. edge disc.
A: 2; B: Sorter clear span; D: =; F: 3420 | 7 | 7 Three edge disc.(one Long edge cont.)
[8 empty] | 8 | 8 Three edge disc.(one short edge cont.)
A: 3; B: Thickness of Slab; D: =; F: 150 | 9 | 9 Four edge disc.
[10 empty] | 1 | 1 | Interior panel
A: 4; B: Total UDL.; D: =; F: 1.2 |  |  | 2 | 2 | one short edge disc.
[10 empty] | 3 | 3 | one long edge disc.
A: 5; B: Support Condition; D: =; F: 1 Interior panel |  |  | 4 | 4 | Two adjacent edge disc.
[10 empty] | 5 | 5 | Two short edge disc.
A: 8; B: A. DESIGN FORCES |  |  | 7 | 7 | Three edge disc.(one Long edge cont.)
9 | Longer clear span |  |  |  | 4235 | <mm; m> | 4.235 |  |  | 7 | 7 | Three edge disc.(one short edge cont.)
10 | Sorter clear span |  |  |  | 3420 | <mm; m> | 3.42 |  |  | 8 | 8 | Four edge disc.
11
12 | Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 150 | <mm; m> | 0.15
| Clear cover to main reinf |  |  |  | 25 | mm
| Maximum diameter of bar |  |  |  | 10 | mm
| Facor of safety |  |  |  | 1.5 | mm
| minimum slab thkness |  |  |  | 110 | mm
| Permissible Mu/bd2 |  |  |  | 2.76
13 |  | OK,More than the min. as per tender.
14 |  | OK, From max. Mu/bd2 considerations as detailed hereunder.
15 |  | OK from deflection considerations as checked hereunder.
16 | The least effective depth in shorter / longer direction |  |  | = 150-25 -10/2 = | 120 | <mm; cm> | 12
17
| Total design UDL |  |  |  | 1.2 | t/m2
19 |  |  |  | Say | 1.2 | t/m2
21
22 | Longer effective span | LY |  | = 4235+120 = | 4355 | <mm; m> | 4.355
23 | Sorter effective span | Lx |  | = 3420+120 = | 3540 | <mm; m> | 3.54
24 |  |  | Ly/Lx | = 4355/3540 = | 1.23
26
27 | Shorter of the two spans (for use in bending moment calculations) |  |  |  | 3540 | <mm; m> | 3.54
28
29 | Refering IS-456, Table-22, P91 |  | 1 | 1 Interior panel
30 | -ve support moment at continuous edge across long span | -My | 0.0442 | = 0.044*1.2*3.54^2 = | 0.66468 | tm
31 | +ve moment at mid span across long span | +My | 0.0332 | = 0.033*1.2*3.54^2 = | 0.49926 | tm
32 | -ve support moment at continuous edge across short span | -Mx | 0.032 | = 0.032*1.2*3.54^2 = | 0.48121 | tm
33 | +ve moment at mid span across short span | +Mx | 0.024 | = 0.024*1.2*3.54^2 = | 0.36091 | tm
34
35 | B. REINFORCEMENTS
36 | -ve Mu/bd2 at support across long span |  | = 1.5*0.66*10000/120^2 = |  | 0.69237 | N/mm2
37 | +ve Mu/bd2 at mid span across long span |  | = 1.5*0.5*10000/120^2 = |  | 0.52006 | N/mm2
38 | -ve Mu/bd2 at support across short span |  | = 1.5*0.48*10000/120^2 = |  | 0.50126 | N/mm2
39 | +ve Mu/bd2 at mid span across short span |  | = 1.5*0.36*10000/120^2 = |  | 0.37595 | N/mm2
40
41 | Max. Mu/bd2 |  |  | Max. of (0.69:0.38) | 0.69237 | N/mm2
44 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
45 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
46
47 |  |  | Reinf as per Table-2,Pg-48,SP-16
48 | Reqd. reinf | Mu/bd2 | ptxd/10
49
50 | For -ve moment i.e. top reinf. across long span | 0.69237 | 0.1644 | = 0.164*12/10 = | 1.9728 | cm2/m
51 | For +ve moment i.e. bottom reinf. across long span | 0.52006 | 0.1228 | = 0.123*12/10 = | 1.4736 | cm2/m
52 | For -ve moment i.e. top reinf. across short span | 0.50126 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
53 | For +ve moment i.e. bottom reinf. across short span | 0.37595 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
54
55 | Main Reinforcements | F | spacing
56 | At top across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
57 | At bottom across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
58 | At top across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
59 | At bottom across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
60 |  |  |  |  | Max. % steel = |  | 0.168
62 | Max. permissible spacing | 3 | 360 | (As per Cl. 26.3.3; Pg. 46; IS:456)
63 |  | or | 300
64 | Least of the two |  | 300
65 | Max. provided spacing |  | 250
66 |  |  | OK
68 | Distribution Reinforcement
69 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
70 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
71 | Provide | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m
72 | Max. permissible spacing | 5 | 600 | (As per Cl. 26.3.3; Pg. 46; IS:456)
73 |  | or | 450
74 | Least of the two |  | 450
75 | Max. provided spacing |  | 250
76 |  |  | OK
78 | C. DEFLECTION CHECK
79 | Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
80 |  |  |  | Cantilever | 7
81 |  |  |  | Simply supported | 20
82 |  |  |  | Continuous | 26
83 | fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 284.4307
| Multiplication factor corresponding to steel service stress of 0.168% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 1.5228
84 | Modified applicable ratio assuming 'Discontinuous' |  |  | = 1.52*26 = | 39.5928
85 | Actual 'Span' to 'Depth' ratio |  |  | = 3420/120 = | 28.5
86 |  | OK from deflection considerations.
87
88 | D. SKETCH
89
90 |  |  |  | 8 | 250
91
92 |  |  | 8 | 250
93
94 | 3420
95 |  |  |  |  | 8 | 250
96 |  |  | 8 | 250
97
98
99 |  | 4235
100 |  |  | PLAN
101
102 |  | All distribution rebars = | 8 | 250
103
104
105 | [5 empty] | 150
106
107
108 |  |  | SECTION
109
110 | Provided rebars on drawings may be the same or greater than the above design requirements.
111
112
113
114
115

## S18 (hidden)
STRUCTURE : |  | ADMIN BUILDING
ITEM : |  | SLAB, S18 | [5 empty] | 1 | 1 Interior panel
Sl. No. | ITEM | NOTN. | FORMULA | CALCULATIONS | VALUE | UNIT | REMARKS | 2 | 2 one short edge disc.
[8 empty] | 3 | 3 one long edge disc.
A | B | C | D | E | F | G | H | 4 | 4 Two adjacent edge disc.
A: 1; B: Longer clear span; D: =; F: 4560 | 5 | 5 Two short edge disc.
[8 empty] | 6 | 6 Two long. edge disc.
A: 2; B: Sorter clear span; D: =; F: 3690 | 7 | 7 Three edge disc.(one Long edge cont.)
[8 empty] | 8 | 8 Three edge disc.(one short edge cont.)
A: 3; B: Thickness of Slab; D: =; F: 150 | 9 | 9 Four edge disc.
[10 empty] | 1 | 1 | Interior panel
A: 4; B: Total UDL.; D: =; F: 1.2 |  |  | 2 | 2 | one short edge disc.
[10 empty] | 3 | 3 | one long edge disc.
A: 5; B: Support Condition; D: =; F: 3 one long edge disc. |  |  | 4 | 4 | Two adjacent edge disc.
[10 empty] | 5 | 5 | Two short edge disc.
A: 8; B: A. DESIGN FORCES |  |  | 7 | 7 | Three edge disc.(one Long edge cont.)
9 | Longer clear span |  |  |  | 4560 | <mm; m> | 4.56 |  |  | 7 | 7 | Three edge disc.(one short edge cont.)
10 | Sorter clear span |  |  |  | 3690 | <mm; m> | 3.69 |  |  | 8 | 8 | Four edge disc.
11
12 | Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 150 | <mm; m> | 0.15
| Clear cover to main reinf |  |  |  | 25 | mm
| Maximum diameter of bar |  |  |  | 10 | mm
| Facor of safety |  |  |  | 1.5 | mm
| minimum slab thkness |  |  |  | 110 | mm
| Permissible Mu/bd2 |  |  |  | 2.76
13 |  | OK,More than the min. as per tender.
14 |  | OK, From max. Mu/bd2 considerations as detailed hereunder.
15 |  | OK from deflection considerations as checked hereunder.
16 | The least effective depth in shorter / longer direction |  |  | = 150-25 -10/2 = | 120 | <mm; cm> | 12
17
| Total design UDL |  |  |  | 1.2 | t/m2
19 |  |  |  | Say | 1.2 | t/m2
21
22 | Longer effective span | LY |  | = 4560+120 = | 4680 | <mm; m> | 4.68
23 | Sorter effective span | Lx |  | = 3690+120 = | 3810 | <mm; m> | 3.81
24 |  |  | Ly/Lx | = 4680/3810 = | 1.23
26
27 | Shorter of the two spans (for use in bending moment calculations) |  |  |  | 3810 | <mm; m> | 3.81
28
29 | Refering IS-456, Table-22, P91 |  | 3 | 3 one long edge disc.
30 | -ve support moment at continuous edge across long span | -My | 0.0535 | = 0.054*1.2*3.81^2 = | 0.93193 | tm
31 | +ve moment at mid span across long span | +My | 0.0405 | = 0.041*1.2*3.81^2 = | 0.70548 | tm
32 | -ve support moment at continuous edge across short span | -Mx | 0.037 | = 0.037*1.2*3.81^2 = | 0.64451 | tm
33 | +ve moment at mid span across short span | +Mx | 0.028 | = 0.028*1.2*3.81^2 = | 0.48774 | tm
34
35 | B. REINFORCEMENTS
36 | -ve Mu/bd2 at support across long span |  | = 1.5*0.93*10000/120^2 = |  | 0.97076 | N/mm2
37 | +ve Mu/bd2 at mid span across long span |  | = 1.5*0.71*10000/120^2 = |  | 0.73488 | N/mm2
38 | -ve Mu/bd2 at support across short span |  | = 1.5*0.64*10000/120^2 = |  | 0.67137 | N/mm2
39 | +ve Mu/bd2 at mid span across short span |  | = 1.5*0.49*10000/120^2 = |  | 0.50806 | N/mm2
40
41 | Max. Mu/bd2 |  |  | Max. of (0.97:0.51) | 0.97076 | N/mm2
44 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
45 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
46
47 |  |  | Reinf as per Table-2,Pg-48,SP-16
48 | Reqd. reinf | Mu/bd2 | ptxd/10
49
50 | For -ve moment i.e. top reinf. across long span | 0.97076 | 0.2342 | = 0.234*12/10 = | 2.8104 | cm2/m
51 | For +ve moment i.e. bottom reinf. across long span | 0.73488 | 0.1748 | = 0.175*12/10 = | 2.0976 | cm2/m
52 | For -ve moment i.e. top reinf. across short span | 0.67137 | 0.1592 | = 0.159*12/10 = | 1.9104 | cm2/m
53 | For +ve moment i.e. bottom reinf. across short span | 0.50806 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
54
55 | Main Reinforcements | F | spacing
56 | At top across long span | 8 | 175 | = pi/4*(8/10)^2*1000/175 = | 2.8735 | cm2/m | 0.239
57 | At bottom across long span | 8 | 200 | = pi/4*(8/10)^2*1000/200 = | 2.5143 | cm2/m | 0.21
58 | At top across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
59 | At bottom across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
60 |  |  |  |  | Max. % steel = |  | 0.239
62 | Max. permissible spacing | 3 | 360 | (As per Cl. 26.3.3; Pg. 46; IS:456)
63 |  | or | 300
64 | Least of the two |  | 300
65 | Max. provided spacing |  | 250
66 |  |  | OK
68 | Distribution Reinforcement
69 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
70 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
71 | Provide | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m
72 | Max. permissible spacing | 5 | 600 | (As per Cl. 26.3.3; Pg. 46; IS:456)
73 |  | or | 450
74 | Least of the two |  | 450
75 | Max. provided spacing |  | 250
76 |  |  | OK
78 | C. DEFLECTION CHECK
79 | Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
80 |  |  |  | Cantilever | 7
81 |  |  |  | Simply supported | 20
82 |  |  |  | Continuous | 26
83 | fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 283.6348
| Multiplication factor corresponding to steel service stress of 0.239% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 1.3337
84 | Modified applicable ratio assuming 'Discontinuous' |  |  | = 1.33*26 = | 34.6758
85 | Actual 'Span' to 'Depth' ratio |  |  | = 3690/120 = | 30.75
86 |  | OK from deflection considerations.
87
88 | D. SKETCH
89
90 |  |  |  | 8 | 175
91
92 |  |  | 8 | 200
93
94 | 3690
95 |  |  |  |  | 8 | 250
96 |  |  | 8 | 250
97
98
99 |  | 4560
100 |  |  | PLAN
101
102 |  | All distribution rebars = | 8 | 250
103
104
105 | [5 empty] | 150
106
107
108 |  |  | SECTION
109
110 | Provided rebars on drawings may be the same or greater than the above design requirements.
111
112
113
114
115

## S19 (hidden)
STRUCTURE : |  | ADMIN BUILDING
ITEM : |  | SLAB, S19 | [5 empty] | 1 | 1 Interior panel
Sl. No. | ITEM | NOTN. | FORMULA | CALCULATIONS | VALUE | UNIT | REMARKS | 2 | 2 one short edge disc.
[8 empty] | 3 | 3 one long edge disc.
A | B | C | D | E | F | G | H | 4 | 4 Two adjacent edge disc.
A: 1; B: Longer clear span; D: =; F: 3420 | 5 | 5 Two short edge disc.
[8 empty] | 6 | 6 Two long. edge disc.
A: 2; B: Sorter clear span; D: =; F: 3240 | 7 | 7 Three edge disc.(one Long edge cont.)
[8 empty] | 8 | 8 Three edge disc.(one short edge cont.)
A: 3; B: Thickness of Slab; D: =; F: 150 | 9 | 9 Four edge disc.
[10 empty] | 1 | 1 | Interior panel
A: 4; B: Total UDL.; D: =; F: 1.2 |  |  | 2 | 2 | one short edge disc.
[10 empty] | 3 | 3 | one long edge disc.
A: 5; B: Support Condition; D: =; F: 1 Interior panel |  |  | 4 | 4 | Two adjacent edge disc.
[10 empty] | 5 | 5 | Two short edge disc.
A: 8; B: A. DESIGN FORCES |  |  | 7 | 7 | Three edge disc.(one Long edge cont.)
9 | Longer clear span |  |  |  | 3420 | <mm; m> | 3.42 |  |  | 7 | 7 | Three edge disc.(one short edge cont.)
10 | Sorter clear span |  |  |  | 3240 | <mm; m> | 3.24 |  |  | 8 | 8 | Four edge disc.
11
12 | Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 150 | <mm; m> | 0.15
| Clear cover to main reinf |  |  |  | 25 | mm
| Maximum diameter of bar |  |  |  | 10 | mm
| Facor of safety |  |  |  | 1.5 | mm
| minimum slab thkness |  |  |  | 110 | mm
| Permissible Mu/bd2 |  |  |  | 2.76
13 |  | OK,More than the min. as per tender.
14 |  | OK, From max. Mu/bd2 considerations as detailed hereunder.
15 |  | OK from deflection considerations as checked hereunder.
16 | The least effective depth in shorter / longer direction |  |  | = 150-25 -10/2 = | 120 | <mm; cm> | 12
17
| Total design UDL |  |  |  | 1.2 | t/m2
19 |  |  |  | Say | 1.2 | t/m2
21
22 | Longer effective span | LY |  | = 3420+120 = | 3540 | <mm; m> | 3.54
23 | Sorter effective span | Lx |  | = 3240+120 = | 3360 | <mm; m> | 3.36
24 |  |  | Ly/Lx | = 3540/3360 = | 1.05
26
27 | Shorter of the two spans (for use in bending moment calculations) |  |  |  | 3360 | <mm; m> | 3.36
28
29 | Refering IS-456, Table-22, P91 |  | 1 | 1 Interior panel
30 | -ve support moment at continuous edge across long span | -My | 0.0345 | = 0.035*1.2*3.36^2 = | 0.46739 | tm
31 | +ve moment at mid span across long span | +My | 0.026 | = 0.026*1.2*3.36^2 = | 0.35224 | tm
32 | -ve support moment at continuous edge across short span | -Mx | 0.032 | = 0.032*1.2*3.36^2 = | 0.43352 | tm
33 | +ve moment at mid span across short span | +Mx | 0.024 | = 0.024*1.2*3.36^2 = | 0.32514 | tm
34
35 | B. REINFORCEMENTS
36 | -ve Mu/bd2 at support across long span |  | = 1.5*0.47*10000/120^2 = |  | 0.48686 | N/mm2
37 | +ve Mu/bd2 at mid span across long span |  | = 1.5*0.35*10000/120^2 = |  | 0.36691 | N/mm2
38 | -ve Mu/bd2 at support across short span |  | = 1.5*0.43*10000/120^2 = |  | 0.45158 | N/mm2
39 | +ve Mu/bd2 at mid span across short span |  | = 1.5*0.33*10000/120^2 = |  | 0.33869 | N/mm2
40
41 | Max. Mu/bd2 |  |  | Max. of (0.49:0.34) | 0.48686 | N/mm2
44 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
45 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
46
47 |  |  | Reinf as per Table-2,Pg-48,SP-16
48 | Reqd. reinf | Mu/bd2 | ptxd/10
49
50 | For -ve moment i.e. top reinf. across long span | 0.48686 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
51 | For +ve moment i.e. bottom reinf. across long span | 0.36691 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
52 | For -ve moment i.e. top reinf. across short span | 0.45158 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
53 | For +ve moment i.e. bottom reinf. across short span | 0.33869 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
54
55 | Main Reinforcements | F | spacing
56 | At top across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
57 | At bottom across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
58 | At top across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
59 | At bottom across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
60 |  |  |  |  | Max. % steel = |  | 0.168
62 | Max. permissible spacing | 3 | 360 | (As per Cl. 26.3.3; Pg. 46; IS:456)
63 |  | or | 300
64 | Least of the two |  | 300
65 | Max. provided spacing |  | 250
66 |  |  | OK
68 | Distribution Reinforcement
69 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
70 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
71 | Provide | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m
72 | Max. permissible spacing | 5 | 600 | (As per Cl. 26.3.3; Pg. 46; IS:456)
73 |  | or | 450
74 | Least of the two |  | 450
75 | Max. provided spacing |  | 250
76 |  |  | OK
78 | C. DEFLECTION CHECK
79 | Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
80 |  |  |  | Cantilever | 7
81 |  |  |  | Simply supported | 20
82 |  |  |  | Continuous | 26
83 | fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 207.6136
| Multiplication factor corresponding to steel service stress of 0.168% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 2
84 | Modified applicable ratio assuming 'Discontinuous' |  |  | = 2*26 = | 52
85 | Actual 'Span' to 'Depth' ratio |  |  | = 3240/120 = | 27
86 |  | OK from deflection considerations.
87
88 | D. SKETCH
89
90 |  |  |  | 8 | 250
91
92 |  |  | 8 | 250
93
94 | 3240
95 |  |  |  |  | 8 | 250
96 |  |  | 8 | 250
97
98
99 |  | 3420
100 |  |  | PLAN
101
102 |  | All distribution rebars = | 8 | 250
103
104
105 | [5 empty] | 150
106
107
108 |  |  | SECTION
109
110 | Provided rebars on drawings may be the same or greater than the above design requirements.
111
112
113
114
115

## S20 (hidden)
STRUCTURE : |  | ADMIN BUILDING
ITEM : |  | SLAB, S20 | [5 empty] | 1 | 1 Interior panel
Sl. No. | ITEM | NOTN. | FORMULA | CALCULATIONS | VALUE | UNIT | REMARKS | 2 | 2 one short edge disc.
[8 empty] | 3 | 3 one long edge disc.
A | B | C | D | E | F | G | H | 4 | 4 Two adjacent edge disc.
A: 1; B: Longer clear span; D: =; F: 5250 | 5 | 5 Two short edge disc.
[8 empty] | 6 | 6 Two long. edge disc.
A: 2; B: Sorter clear span; D: =; F: 3095 | 7 | 7 Three edge disc.(one Long edge cont.)
[8 empty] | 8 | 8 Three edge disc.(one short edge cont.)
A: 3; B: Thickness of Slab; D: =; F: 150 | 9 | 9 Four edge disc.
[10 empty] | 1 | 1 | Interior panel
A: 4; B: Total UDL.; D: =; F: 1.2 |  |  | 2 | 2 | one short edge disc.
[10 empty] | 3 | 3 | one long edge disc.
A: 5; B: Support Condition; D: =; F: 4 Two adjacent edge disc. |  |  | 4 | 4 | Two adjacent edge disc.
[10 empty] | 5 | 5 | Two short edge disc.
A: 8; B: A. DESIGN FORCES |  |  | 7 | 7 | Three edge disc.(one Long edge cont.)
9 | Longer clear span |  |  |  | 5250 | <mm; m> | 5.25 |  |  | 7 | 7 | Three edge disc.(one short edge cont.)
10 | Sorter clear span |  |  |  | 3095 | <mm; m> | 3.095 |  |  | 8 | 8 | Four edge disc.
11
12 | Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 150 | <mm; m> | 0.15
| Clear cover to main reinf |  |  |  | 25 | mm
| Maximum diameter of bar |  |  |  | 10 | mm
| Facor of safety |  |  |  | 1.5 | mm
| minimum slab thkness |  |  |  | 110 | mm
| Permissible Mu/bd2 |  |  |  | 2.76
13 |  | OK,More than the min. as per tender.
14 |  | OK, From max. Mu/bd2 considerations as detailed hereunder.
15 |  | OK from deflection considerations as checked hereunder.
16 | The least effective depth in shorter / longer direction |  |  | = 150-25 -10/2 = | 120 | <mm; cm> | 12
17
| Total design UDL |  |  |  | 1.2 | t/m2
19 |  |  |  | Say | 1.2 | t/m2
21
22 | Longer effective span | LY |  | = 5250+120 = | 5370 | <mm; m> | 5.37
23 | Sorter effective span | Lx |  | = 3095+120 = | 3215 | <mm; m> | 3.215
24 |  |  | Ly/Lx | = 5370/3215 = | 1.67
26
27 | Shorter of the two spans (for use in bending moment calculations) |  |  |  | 3215 | <mm; m> | 3.215
28
29 | Refering IS-456, Table-22, P91 |  | 4 | 4 Two adjacent edge disc.
30 | -ve support moment at continuous edge across long span | -My | 0.08112 | = 0.081*1.2*3.22^2 = | 1.0062 | tm
31 | +ve moment at mid span across long span | +My | 0.06076 | = 0.061*1.2*3.22^2 = | 0.75363 | tm
32 | -ve support moment at continuous edge across short span | -Mx | 0.047 | = 0.047*1.2*3.22^2 = | 0.58296 | tm
33 | +ve moment at mid span across short span | +Mx | 0.035 | = 0.035*1.2*3.22^2 = | 0.43412 | tm
34
35 | B. REINFORCEMENTS
36 | -ve Mu/bd2 at support across long span |  | = 1.5*1.01*10000/120^2 = |  | 1.0481 | N/mm2
37 | +ve Mu/bd2 at mid span across long span |  | = 1.5*0.75*10000/120^2 = |  | 0.78504 | N/mm2
38 | -ve Mu/bd2 at support across short span |  | = 1.5*0.58*10000/120^2 = |  | 0.60725 | N/mm2
39 | +ve Mu/bd2 at mid span across short span |  | = 1.5*0.43*10000/120^2 = |  | 0.45221 | N/mm2
40
41 | Max. Mu/bd2 |  |  | Max. of (1.05:0.45) | 1.0481 | N/mm2
44 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
45 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
46
47 |  |  | Reinf as per Table-2,Pg-48,SP-16
48 | Reqd. reinf | Mu/bd2 | ptxd/10
49
50 | For -ve moment i.e. top reinf. across long span | 1.0481 | 0.2524 | = 0.252*12/10 = | 3.0288 | cm2/m
51 | For +ve moment i.e. bottom reinf. across long span | 0.78504 | 0.1862 | = 0.186*12/10 = | 2.2344 | cm2/m
52 | For -ve moment i.e. top reinf. across short span | 0.60725 | 0.142 | = 0.142*12/10 = | 1.704 | cm2/m
53 | For +ve moment i.e. bottom reinf. across short span | 0.45221 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
54
55 | Main Reinforcements | F | spacing
56 | At top across long span | 8 | 150 | = pi/4*(8/10)^2*1000/150 = | 3.3524 | cm2/m | 0.279
57 | At bottom across long span | 8 | 200 | = pi/4*(8/10)^2*1000/200 = | 2.5143 | cm2/m | 0.21
58 | At top across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
59 | At bottom across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
60 |  |  |  |  | Max. % steel = |  | 0.279
62 | Max. permissible spacing | 3 | 360 | (As per Cl. 26.3.3; Pg. 46; IS:456)
63 |  | or | 300
64 | Least of the two |  | 300
65 | Max. provided spacing |  | 250
66 |  |  | OK
68 | Distribution Reinforcement
69 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
70 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
71 | Provide | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m
72 | Max. permissible spacing | 5 | 600 | (As per Cl. 26.3.3; Pg. 46; IS:456)
73 |  | or | 450
74 | Least of the two |  | 450
75 | Max. provided spacing |  | 250
76 |  |  | OK
78 | C. DEFLECTION CHECK
79 | Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
80 |  |  |  | Cantilever | 7
81 |  |  |  | Simply supported | 20
82 |  |  |  | Continuous | 26
83 | fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 262.0084
| Multiplication factor corresponding to steel service stress of 0.279% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 1.3847
84 | Modified applicable ratio assuming 'Discontinuous' |  |  | = 1.38*26 = | 36.0026
85 | Actual 'Span' to 'Depth' ratio |  |  | = 3095/120 = | 25.7917
86 |  | OK from deflection considerations.
87
88 | D. SKETCH
89
90 |  |  |  | 8 | 150
91
92 |  |  | 8 | 200
93
94 | 3095
95 |  |  |  |  | 8 | 250
96 |  |  | 8 | 250
97
98
99 |  | 5250
100 |  |  | PLAN
101
102 |  | All distribution rebars = | 8 | 250
103
104
105 | [5 empty] | 150
106
107
108 |  |  | SECTION
109
110 | Provided rebars on drawings may be the same or greater than the above design requirements.
111
112
113
114
115

## S21 (hidden)
STRUCTURE : |  | ADMIN BUILDING
ITEM : |  | SLAB, S21 | [5 empty] | 1 | 1 Interior panel
Sl. No. | ITEM | NOTN. | FORMULA | CALCULATIONS | VALUE | UNIT | REMARKS | 2 | 2 one short edge disc.
[8 empty] | 3 | 3 one long edge disc.
A | B | C | D | E | F | G | H | 4 | 4 Two adjacent edge disc.
A: 1; B: Longer clear span; D: =; F: 4635 | 5 | 5 Two short edge disc.
[8 empty] | 6 | 6 Two long. edge disc.
A: 2; B: Sorter clear span; D: =; F: 3095 | 7 | 7 Three edge disc.(one Long edge cont.)
[8 empty] | 8 | 8 Three edge disc.(one short edge cont.)
A: 3; B: Thickness of Slab; D: =; F: 150 | 9 | 9 Four edge disc.
[10 empty] | 1 | 1 | Interior panel
A: 4; B: Total UDL.; D: =; F: 1.2 |  |  | 2 | 2 | one short edge disc.
[10 empty] | 3 | 3 | one long edge disc.
A: 5; B: Support Condition; D: =; F: 1 Interior panel |  |  | 4 | 4 | Two adjacent edge disc.
[10 empty] | 5 | 5 | Two short edge disc.
A: 8; B: A. DESIGN FORCES |  |  | 7 | 7 | Three edge disc.(one Long edge cont.)
9 | Longer clear span |  |  |  | 4635 | <mm; m> | 4.635 |  |  | 7 | 7 | Three edge disc.(one short edge cont.)
10 | Sorter clear span |  |  |  | 3095 | <mm; m> | 3.095 |  |  | 8 | 8 | Four edge disc.
11
12 | Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 150 | <mm; m> | 0.15
| Clear cover to main reinf |  |  |  | 25 | mm
| Maximum diameter of bar |  |  |  | 10 | mm
| Facor of safety |  |  |  | 1.5 | mm
| minimum slab thkness |  |  |  | 110 | mm
| Permissible Mu/bd2 |  |  |  | 2.76
13 |  | OK,More than the min. as per tender.
14 |  | OK, From max. Mu/bd2 considerations as detailed hereunder.
15 |  | OK from deflection considerations as checked hereunder.
16 | The least effective depth in shorter / longer direction |  |  | = 150-25 -10/2 = | 120 | <mm; cm> | 12
17
| Total design UDL |  |  |  | 1.2 | t/m2
19 |  |  |  | Say | 1.2 | t/m2
21
22 | Longer effective span | LY |  | = 4635+120 = | 4755 | <mm; m> | 4.755
23 | Sorter effective span | Lx |  | = 3095+120 = | 3215 | <mm; m> | 3.215
24 |  |  | Ly/Lx | = 4755/3215 = | 1.48
26
27 | Shorter of the two spans (for use in bending moment calculations) |  |  |  | 3215 | <mm; m> | 3.215
28
29 | Refering IS-456, Table-22, P91 |  | 1 | 1 Interior panel
30 | -ve support moment at continuous edge across long span | -My | 0.0526 | = 0.053*1.2*3.22^2 = | 0.65242 | tm
31 | +ve moment at mid span across long span | +My | 0.0406 | = 0.041*1.2*3.22^2 = | 0.50358 | tm
32 | -ve support moment at continuous edge across short span | -Mx | 0.032 | = 0.032*1.2*3.22^2 = | 0.39691 | tm
33 | +ve moment at mid span across short span | +Mx | 0.024 | = 0.024*1.2*3.22^2 = | 0.29768 | tm
34
35 | B. REINFORCEMENTS
36 | -ve Mu/bd2 at support across long span |  | = 1.5*0.65*10000/120^2 = |  | 0.67961 | N/mm2
37 | +ve Mu/bd2 at mid span across long span |  | = 1.5*0.5*10000/120^2 = |  | 0.52456 | N/mm2
38 | -ve Mu/bd2 at support across short span |  | = 1.5*0.4*10000/120^2 = |  | 0.41345 | N/mm2
39 | +ve Mu/bd2 at mid span across short span |  | = 1.5*0.3*10000/120^2 = |  | 0.31009 | N/mm2
40
41 | Max. Mu/bd2 |  |  | Max. of (0.68:0.31) | 0.67961 | N/mm2
44 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
45 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
46
47 |  |  | Reinf as per Table-2,Pg-48,SP-16
48 | Reqd. reinf | Mu/bd2 | ptxd/10
49
50 | For -ve moment i.e. top reinf. across long span | 0.67961 | 0.1592 | = 0.159*12/10 = | 1.9104 | cm2/m
51 | For +ve moment i.e. bottom reinf. across long span | 0.52456 | 0.1228 | = 0.123*12/10 = | 1.4736 | cm2/m
52 | For -ve moment i.e. top reinf. across short span | 0.41345 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
53 | For +ve moment i.e. bottom reinf. across short span | 0.31009 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
54
55 | Main Reinforcements | F | spacing
56 | At top across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
57 | At bottom across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
58 | At top across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
59 | At bottom across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
60 |  |  |  |  | Max. % steel = |  | 0.168
62 | Max. permissible spacing | 3 | 360 | (As per Cl. 26.3.3; Pg. 46; IS:456)
63 |  | or | 300
64 | Least of the two |  | 300
65 | Max. provided spacing |  | 250
66 |  |  | OK
68 | Distribution Reinforcement
69 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
70 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
71 | Provide | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m
72 | Max. permissible spacing | 5 | 600 | (As per Cl. 26.3.3; Pg. 46; IS:456)
73 |  | or | 450
74 | Least of the two |  | 450
75 | Max. provided spacing |  | 250
76 |  |  | OK
78 | C. DEFLECTION CHECK
79 | Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
80 |  |  |  | Cantilever | 7
81 |  |  |  | Simply supported | 20
82 |  |  |  | Continuous | 26
83 | fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 275.4341
| Multiplication factor corresponding to steel service stress of 0.168% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 1.5931
84 | Modified applicable ratio assuming 'Discontinuous' |  |  | = 1.59*26 = | 41.42
85 | Actual 'Span' to 'Depth' ratio |  |  | = 3095/120 = | 25.7917
86 |  | OK from deflection considerations.
87
88 | D. SKETCH
89
90 |  |  |  | 8 | 250
91
92 |  |  | 8 | 250
93
94 | 3095
95 |  |  |  |  | 8 | 250
96 |  |  | 8 | 250
97
98
99 |  | 4635
100 |  |  | PLAN
101
102 |  | All distribution rebars = | 8 | 250
103
104
105 | [5 empty] | 150
106
107
108 |  |  | SECTION
109
110 | Provided rebars on drawings may be the same or greater than the above design requirements.
111
112
113
114
115

## S22 (hidden)
STRUCTURE : |  | ADMIN BUILDING
ITEM : |  | SLAB, S22 | [5 empty] | 1 | 1 Interior panel
Sl. No. | ITEM | NOTN. | FORMULA | CALCULATIONS | VALUE | UNIT | REMARKS | 2 | 2 one short edge disc.
[8 empty] | 3 | 3 one long edge disc.
A | B | C | D | E | F | G | H | 4 | 4 Two adjacent edge disc.
A: 1; B: Longer clear span; D: =; F: 4635 | 5 | 5 Two short edge disc.
[8 empty] | 6 | 6 Two long. edge disc.
A: 2; B: Sorter clear span; D: =; F: 3095 | 7 | 7 Three edge disc.(one Long edge cont.)
[8 empty] | 8 | 8 Three edge disc.(one short edge cont.)
A: 3; B: Thickness of Slab; D: =; F: 150 | 9 | 9 Four edge disc.
[10 empty] | 1 | 1 | Interior panel
A: 4; B: Total UDL.; D: =; F: 1.2 |  |  | 2 | 2 | one short edge disc.
[10 empty] | 3 | 3 | one long edge disc.
A: 5; B: Support Condition; D: =; F: 1 Interior panel |  |  | 4 | 4 | Two adjacent edge disc.
[10 empty] | 5 | 5 | Two short edge disc.
A: 8; B: A. DESIGN FORCES |  |  | 7 | 7 | Three edge disc.(one Long edge cont.)
9 | Longer clear span |  |  |  | 4635 | <mm; m> | 4.635 |  |  | 7 | 7 | Three edge disc.(one short edge cont.)
10 | Sorter clear span |  |  |  | 3095 | <mm; m> | 3.095 |  |  | 8 | 8 | Four edge disc.
11
12 | Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 150 | <mm; m> | 0.15
| Clear cover to main reinf |  |  |  | 25 | mm
| Maximum diameter of bar |  |  |  | 10 | mm
| Facor of safety |  |  |  | 1.5 | mm
| minimum slab thkness |  |  |  | 110 | mm
| Permissible Mu/bd2 |  |  |  | 2.76
13 |  | OK,More than the min. as per tender.
14 |  | OK, From max. Mu/bd2 considerations as detailed hereunder.
15 |  | OK from deflection considerations as checked hereunder.
16 | The least effective depth in shorter / longer direction |  |  | = 150-25 -10/2 = | 120 | <mm; cm> | 12
17
| Total design UDL |  |  |  | 1.2 | t/m2
19 |  |  |  | Say | 1.2 | t/m2
21
22 | Longer effective span | LY |  | = 4635+120 = | 4755 | <mm; m> | 4.755
23 | Sorter effective span | Lx |  | = 3095+120 = | 3215 | <mm; m> | 3.215
24 |  |  | Ly/Lx | = 4755/3215 = | 1.48
26
27 | Shorter of the two spans (for use in bending moment calculations) |  |  |  | 3215 | <mm; m> | 3.215
28
29 | Refering IS-456, Table-22, P91 |  | 1 | 1 Interior panel
30 | -ve support moment at continuous edge across long span | -My | 0.0526 | = 0.053*1.2*3.22^2 = | 0.65242 | tm
31 | +ve moment at mid span across long span | +My | 0.0406 | = 0.041*1.2*3.22^2 = | 0.50358 | tm
32 | -ve support moment at continuous edge across short span | -Mx | 0.032 | = 0.032*1.2*3.22^2 = | 0.39691 | tm
33 | +ve moment at mid span across short span | +Mx | 0.024 | = 0.024*1.2*3.22^2 = | 0.29768 | tm
34
35 | B. REINFORCEMENTS
36 | -ve Mu/bd2 at support across long span |  | = 1.5*0.65*10000/120^2 = |  | 0.67961 | N/mm2
37 | +ve Mu/bd2 at mid span across long span |  | = 1.5*0.5*10000/120^2 = |  | 0.52456 | N/mm2
38 | -ve Mu/bd2 at support across short span |  | = 1.5*0.4*10000/120^2 = |  | 0.41345 | N/mm2
39 | +ve Mu/bd2 at mid span across short span |  | = 1.5*0.3*10000/120^2 = |  | 0.31009 | N/mm2
40
41 | Max. Mu/bd2 |  |  | Max. of (0.68:0.31) | 0.67961 | N/mm2
44 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
45 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
46
47 |  |  | Reinf as per Table-2,Pg-48,SP-16
48 | Reqd. reinf | Mu/bd2 | ptxd/10
49
50 | For -ve moment i.e. top reinf. across long span | 0.67961 | 0.1592 | = 0.159*12/10 = | 1.9104 | cm2/m
51 | For +ve moment i.e. bottom reinf. across long span | 0.52456 | 0.1228 | = 0.123*12/10 = | 1.4736 | cm2/m
52 | For -ve moment i.e. top reinf. across short span | 0.41345 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
53 | For +ve moment i.e. bottom reinf. across short span | 0.31009 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
54
55 | Main Reinforcements | F | spacing
56 | At top across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
57 | At bottom across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
58 | At top across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
59 | At bottom across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
60 |  |  |  |  | Max. % steel = |  | 0.168
62 | Max. permissible spacing | 3 | 360 | (As per Cl. 26.3.3; Pg. 46; IS:456)
63 |  | or | 300
64 | Least of the two |  | 300
65 | Max. provided spacing |  | 250
66 |  |  | OK
68 | Distribution Reinforcement
69 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
70 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
71 | Provide | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m
72 | Max. permissible spacing | 5 | 600 | (As per Cl. 26.3.3; Pg. 46; IS:456)
73 |  | or | 450
74 | Least of the two |  | 450
75 | Max. provided spacing |  | 250
76 |  |  | OK
78 | C. DEFLECTION CHECK
79 | Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
80 |  |  |  | Cantilever | 7
81 |  |  |  | Simply supported | 20
82 |  |  |  | Continuous | 26
83 | fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 275.4341
| Multiplication factor corresponding to steel service stress of 0.168% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 1.5931
84 | Modified applicable ratio assuming 'Discontinuous' |  |  | = 1.59*26 = | 41.42
85 | Actual 'Span' to 'Depth' ratio |  |  | = 3095/120 = | 25.7917
86 |  | OK from deflection considerations.
87
88 | D. SKETCH
89
90 |  |  |  | 8 | 250
91
92 |  |  | 8 | 250
93
94 | 3095
95 |  |  |  |  | 8 | 250
96 |  |  | 8 | 250
97
98
99 |  | 4635
100 |  |  | PLAN
101
102 |  | All distribution rebars = | 8 | 250
103
104
105 | [5 empty] | 150
106
107
108 |  |  | SECTION
109
110 | Provided rebars on drawings may be the same or greater than the above design requirements.
111
112
113
114
115

## S23 (hidden)
STRUCTURE : |  | ADMIN BUILDING
ITEM : |  | SLAB, S23 | [5 empty] | 1 | 1 Interior panel
Sl. No. | ITEM | NOTN. | FORMULA | CALCULATIONS | VALUE | UNIT | REMARKS | 2 | 2 one short edge disc.
[8 empty] | 3 | 3 one long edge disc.
A | B | C | D | E | F | G | H | 4 | 4 Two adjacent edge disc.
A: 1; B: Longer clear span; D: =; F: 4660 | 5 | 5 Two short edge disc.
[8 empty] | 6 | 6 Two long. edge disc.
A: 2; B: Sorter clear span; D: =; F: 2350 | 7 | 7 Three edge disc.(one Long edge cont.)
[8 empty] | 8 | 8 Three edge disc.(one short edge cont.)
A: 3; B: Thickness of Slab; D: =; F: 150 | 9 | 9 Four edge disc.
[10 empty] | 1 | 1 | Interior panel
A: 4; B: Total UDL.; D: =; F: 1.2 |  |  | 2 | 2 | one short edge disc.
[10 empty] | 3 | 3 | one long edge disc.
A: 5; B: Support Condition; D: =; F: 4 Two adjacent edge disc. |  |  | 4 | 4 | Two adjacent edge disc.
[10 empty] | 5 | 5 | Two short edge disc.
A: 8; B: A. DESIGN FORCES |  |  | 7 | 7 | Three edge disc.(one Long edge cont.)
9 | Longer clear span |  |  |  | 4660 | <mm; m> | 4.66 |  |  | 7 | 7 | Three edge disc.(one short edge cont.)
10 | Sorter clear span |  |  |  | 2350 | <mm; m> | 2.35 |  |  | 8 | 8 | Four edge disc.
11
12 | Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 150 | <mm; m> | 0.15
| Clear cover to main reinf |  |  |  | 25 | mm
| Maximum diameter of bar |  |  |  | 10 | mm
| Facor of safety |  |  |  | 1.5 | mm
| minimum slab thkness |  |  |  | 110 | mm
| Permissible Mu/bd2 |  |  |  | 2.76
13 |  | OK,More than the min. as per tender.
14 |  | OK, From max. Mu/bd2 considerations as detailed hereunder.
15 |  | OK from deflection considerations as checked hereunder.
16 | The least effective depth in shorter / longer direction |  |  | = 150-25 -10/2 = | 120 | <mm; cm> | 12
17
| Total design UDL |  |  |  | 1.2 | t/m2
19 |  |  |  | Say | 1.2 | t/m2
21
22 | Longer effective span | LY |  | = 4660+120 = | 4780 | <mm; m> | 4.78
23 | Sorter effective span | Lx |  | = 2350+120 = | 2470 | <mm; m> | 2.47
24 |  |  | Ly/Lx | = 4780/2470 = | 1.94
26
27 | Shorter of the two spans (for use in bending moment calculations) |  |  |  | 2470 | <mm; m> | 2.47
28
29 | Refering IS-456, Table-22, P91 |  | 4 | 4 Two adjacent edge disc.
30 | -ve support moment at continuous edge across long span | -My | 0.08932 | = 0.089*1.2*2.47^2 = | 0.65392 | tm
31 | +ve moment at mid span across long span | +My | 0.06756 | = 0.068*1.2*2.47^2 = | 0.49461 | tm
32 | -ve support moment at continuous edge across short span | -Mx | 0.047 | = 0.047*1.2*2.47^2 = | 0.34409 | tm
33 | +ve moment at mid span across short span | +Mx | 0.035 | = 0.035*1.2*2.47^2 = | 0.25624 | tm
34
35 | B. REINFORCEMENTS
36 | -ve Mu/bd2 at support across long span |  | = 1.5*0.65*10000/120^2 = |  | 0.68117 | N/mm2
37 | +ve Mu/bd2 at mid span across long span |  | = 1.5*0.49*10000/120^2 = |  | 0.51522 | N/mm2
38 | -ve Mu/bd2 at support across short span |  | = 1.5*0.34*10000/120^2 = |  | 0.35843 | N/mm2
39 | +ve Mu/bd2 at mid span across short span |  | = 1.5*0.26*10000/120^2 = |  | 0.26691 | N/mm2
40
41 | Max. Mu/bd2 |  |  | Max. of (0.68:0.27) | 0.68117 | N/mm2
44 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
45 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
46
47 |  |  | Reinf as per Table-2,Pg-48,SP-16
48 | Reqd. reinf | Mu/bd2 | ptxd/10
49
50 | For -ve moment i.e. top reinf. across long span | 0.68117 | 0.1618 | = 0.162*12/10 = | 1.9416 | cm2/m
51 | For +ve moment i.e. bottom reinf. across long span | 0.51522 | 0.1204 | = 0.12*12/10 = | 1.4448 | cm2/m
52 | For -ve moment i.e. top reinf. across short span | 0.35843 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
53 | For +ve moment i.e. bottom reinf. across short span | 0.26691 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
54
55 | Main Reinforcements | F | spacing
56 | At top across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
57 | At bottom across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
58 | At top across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
59 | At bottom across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
60 |  |  |  |  | Max. % steel = |  | 0.168
62 | Max. permissible spacing | 3 | 360 | (As per Cl. 26.3.3; Pg. 46; IS:456)
63 |  | or | 300
64 | Least of the two |  | 300
65 | Max. provided spacing |  | 250
66 |  |  | OK
68 | Distribution Reinforcement
69 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
70 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
71 | Provide | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m
72 | Max. permissible spacing | 5 | 600 | (As per Cl. 26.3.3; Pg. 46; IS:456)
73 |  | or | 450
74 | Least of the two |  | 450
75 | Max. provided spacing |  | 250
76 |  |  | OK
78 | C. DEFLECTION CHECK
79 | Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
80 |  |  |  | Cantilever | 7
81 |  |  |  | Simply supported | 20
82 |  |  |  | Continuous | 26
83 | fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 279.9324
| Multiplication factor corresponding to steel service stress of 0.168% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 1.5571
84 | Modified applicable ratio assuming 'Discontinuous' |  |  | = 1.56*26 = | 40.4858
85 | Actual 'Span' to 'Depth' ratio |  |  | = 2350/120 = | 19.5833
86 |  | OK from deflection considerations.
87
88 | D. SKETCH
89
90 |  |  |  | 8 | 250
91
92 |  |  | 8 | 250
93
94 | 2350
95 |  |  |  |  | 8 | 250
96 |  |  | 8 | 250
97
98
99 |  | 4660
100 |  |  | PLAN
101
102 |  | All distribution rebars = | 8 | 250
103
104
105 | [5 empty] | 150
106
107
108 |  |  | SECTION
109
110 | Provided rebars on drawings may be the same or greater than the above design requirements.
111
112
113
114
115

## S24 (hidden)
STRUCTURE : |  | ADMIN BUILDING
ITEM : |  | SLAB, S24 | [5 empty] | 1 | 1 Interior panel
Sl. No. | ITEM | NOTN. | FORMULA | CALCULATIONS | VALUE | UNIT | REMARKS | 2 | 2 one short edge disc.
[8 empty] | 3 | 3 one long edge disc.
A | B | C | D | E | F | G | H | 4 | 4 Two adjacent edge disc.
A: 1; B: Longer clear span; D: =; F: 4635 | 5 | 5 Two short edge disc.
[8 empty] | 6 | 6 Two long. edge disc.
A: 2; B: Sorter clear span; D: =; F: 2350 | 7 | 7 Three edge disc.(one Long edge cont.)
[8 empty] | 8 | 8 Three edge disc.(one short edge cont.)
A: 3; B: Thickness of Slab; D: =; F: 150 | 9 | 9 Four edge disc.
[10 empty] | 1 | 1 | Interior panel
A: 4; B: Total UDL.; D: =; F: 1.2 |  |  | 2 | 2 | one short edge disc.
[10 empty] | 3 | 3 | one long edge disc.
A: 5; B: Support Condition; D: =; F: 1 Interior panel |  |  | 4 | 4 | Two adjacent edge disc.
[10 empty] | 5 | 5 | Two short edge disc.
A: 8; B: A. DESIGN FORCES |  |  | 7 | 7 | Three edge disc.(one Long edge cont.)
9 | Longer clear span |  |  |  | 4635 | <mm; m> | 4.635 |  |  | 7 | 7 | Three edge disc.(one short edge cont.)
10 | Sorter clear span |  |  |  | 2350 | <mm; m> | 2.35 |  |  | 8 | 8 | Four edge disc.
11
12 | Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 150 | <mm; m> | 0.15
| Clear cover to main reinf |  |  |  | 25 | mm
| Maximum diameter of bar |  |  |  | 10 | mm
| Facor of safety |  |  |  | 1.5 | mm
| minimum slab thkness |  |  |  | 110 | mm
| Permissible Mu/bd2 |  |  |  | 2.76
13 |  | OK,More than the min. as per tender.
14 |  | OK, From max. Mu/bd2 considerations as detailed hereunder.
15 |  | OK from deflection considerations as checked hereunder.
16 | The least effective depth in shorter / longer direction |  |  | = 150-25 -10/2 = | 120 | <mm; cm> | 12
17
| Total design UDL |  |  |  | 1.2 | t/m2
19 |  |  |  | Say | 1.2 | t/m2
21
22 | Longer effective span | LY |  | = 4635+120 = | 4755 | <mm; m> | 4.755
23 | Sorter effective span | Lx |  | = 2350+120 = | 2470 | <mm; m> | 2.47
24 |  |  | Ly/Lx | = 4755/2470 = | 1.93
26
27 | Shorter of the two spans (for use in bending moment calculations) |  |  |  | 2470 | <mm; m> | 2.47
28
29 | Refering IS-456, Table-22, P91 |  | 1 | 1 Interior panel
30 | -ve support moment at continuous edge across long span | -My | 0.0636 | = 0.064*1.2*2.47^2 = | 0.46562 | tm
31 | +ve moment at mid span across long span | +My | 0.04788 | = 0.048*1.2*2.47^2 = | 0.35053 | tm
32 | -ve support moment at continuous edge across short span | -Mx | 0.032 | = 0.032*1.2*2.47^2 = | 0.23427 | tm
33 | +ve moment at mid span across short span | +Mx | 0.024 | = 0.024*1.2*2.47^2 = | 0.17571 | tm
34
35 | B. REINFORCEMENTS
36 | -ve Mu/bd2 at support across long span |  | = 1.5*0.47*10000/120^2 = |  | 0.48502 | N/mm2
37 | +ve Mu/bd2 at mid span across long span |  | = 1.5*0.35*10000/120^2 = |  | 0.36514 | N/mm2
38 | -ve Mu/bd2 at support across short span |  | = 1.5*0.23*10000/120^2 = |  | 0.24404 | N/mm2
39 | +ve Mu/bd2 at mid span across short span |  | = 1.5*0.18*10000/120^2 = |  | 0.18303 | N/mm2
40
41 | Max. Mu/bd2 |  |  | Max. of (0.49:0.18) | 0.48502 | N/mm2
44 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
45 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
46
47 |  |  | Reinf as per Table-2,Pg-48,SP-16
48 | Reqd. reinf | Mu/bd2 | ptxd/10
49
50 | For -ve moment i.e. top reinf. across long span | 0.48502 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
51 | For +ve moment i.e. bottom reinf. across long span | 0.36514 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
52 | For -ve moment i.e. top reinf. across short span | 0.24404 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
53 | For +ve moment i.e. bottom reinf. across short span | 0.18303 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
54
55 | Main Reinforcements | F | spacing
56 | At top across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
57 | At bottom across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
58 | At top across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
59 | At bottom across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
60 |  |  |  |  | Max. % steel = |  | 0.168
62 | Max. permissible spacing | 3 | 360 | (As per Cl. 26.3.3; Pg. 46; IS:456)
63 |  | or | 300
64 | Least of the two |  | 300
65 | Max. provided spacing |  | 250
66 |  |  | OK
68 | Distribution Reinforcement
69 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
70 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
71 | Provide | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m
72 | Max. permissible spacing | 5 | 600 | (As per Cl. 26.3.3; Pg. 46; IS:456)
73 |  | or | 450
74 | Least of the two |  | 450
75 | Max. provided spacing |  | 250
76 |  |  | OK
78 | C. DEFLECTION CHECK
79 | Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
80 |  |  |  | Cantilever | 7
81 |  |  |  | Simply supported | 20
82 |  |  |  | Continuous | 26
83 | fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 207.6136
| Multiplication factor corresponding to steel service stress of 0.168% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 2
84 | Modified applicable ratio assuming 'Discontinuous' |  |  | = 2*26 = | 52
85 | Actual 'Span' to 'Depth' ratio |  |  | = 2350/120 = | 19.5833
86 |  | OK from deflection considerations.
87
88 | D. SKETCH
89
90 |  |  |  | 8 | 250
91
92 |  |  | 8 | 250
93
94 | 2350
95 |  |  |  |  | 8 | 250
96 |  |  | 8 | 250
97
98
99 |  | 4635
100 |  |  | PLAN
101
102 |  | All distribution rebars = | 8 | 250
103
104
105 | [5 empty] | 150
106
107
108 |  |  | SECTION
109
110 | Provided rebars on drawings may be the same or greater than the above design requirements.
111
112
113
114
115

## S25 (hidden)
STRUCTURE : |  | ADMIN BUILDING
ITEM : |  | SLAB, S25 | [5 empty] | 1 | 1 Interior panel
Sl. No. | ITEM | NOTN. | FORMULA | CALCULATIONS | VALUE | UNIT | REMARKS | 2 | 2 one short edge disc.
[8 empty] | 3 | 3 one long edge disc.
A | B | C | D | E | F | G | H | 4 | 4 Two adjacent edge disc.
A: 1; B: Longer clear span; D: =; F: 4660 | 5 | 5 Two short edge disc.
[8 empty] | 6 | 6 Two long. edge disc.
A: 2; B: Sorter clear span; D: =; F: 2750 | 7 | 7 Three edge disc.(one Long edge cont.)
[8 empty] | 8 | 8 Three edge disc.(one short edge cont.)
A: 3; B: Thickness of Slab; D: =; F: 150 | 9 | 9 Four edge disc.
[10 empty] | 1 | 1 | Interior panel
A: 4; B: Total UDL.; D: =; F: 1.2 |  |  | 2 | 2 | one short edge disc.
[10 empty] | 3 | 3 | one long edge disc.
A: 5; B: Support Condition; D: =; F: 2 one short edge disc. |  |  | 4 | 4 | Two adjacent edge disc.
[10 empty] | 5 | 5 | Two short edge disc.
A: 8; B: A. DESIGN FORCES |  |  | 7 | 7 | Three edge disc.(one Long edge cont.)
9 | Longer clear span |  |  |  | 4660 | <mm; m> | 4.66 |  |  | 7 | 7 | Three edge disc.(one short edge cont.)
10 | Sorter clear span |  |  |  | 2750 | <mm; m> | 2.75 |  |  | 8 | 8 | Four edge disc.
11
12 | Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 150 | <mm; m> | 0.15
| Clear cover to main reinf |  |  |  | 25 | mm
| Maximum diameter of bar |  |  |  | 10 | mm
| Facor of safety |  |  |  | 1.5 | mm
| minimum slab thkness |  |  |  | 110 | mm
| Permissible Mu/bd2 |  |  |  | 2.76
13 |  | OK,More than the min. as per tender.
14 |  | OK, From max. Mu/bd2 considerations as detailed hereunder.
15 |  | OK from deflection considerations as checked hereunder.
16 | The least effective depth in shorter / longer direction |  |  | = 150-25 -10/2 = | 120 | <mm; cm> | 12
17
| Total design UDL |  |  |  | 1.2 | t/m2
19 |  |  |  | Say | 1.2 | t/m2
21
22 | Longer effective span | LY |  | = 4660+120 = | 4780 | <mm; m> | 4.78
23 | Sorter effective span | Lx |  | = 2750+120 = | 2870 | <mm; m> | 2.87
24 |  |  | Ly/Lx | = 4780/2870 = | 1.67
26
27 | Shorter of the two spans (for use in bending moment calculations) |  |  |  | 2870 | <mm; m> | 2.87
28
29 | Refering IS-456, Table-22, P91 |  | 2 | 2 one short edge disc.
30 | -ve support moment at continuous edge across long span | -My | 0.06176 | = 0.062*1.2*2.87^2 = | 0.61045 | tm
31 | +ve moment at mid span across long span | +My | 0.04672 | = 0.047*1.2*2.87^2 = | 0.46179 | tm
32 | -ve support moment at continuous edge across short span | -Mx | 0.037 | = 0.037*1.2*2.87^2 = | 0.36572 | tm
33 | +ve moment at mid span across short span | +Mx | 0.028 | = 0.028*1.2*2.87^2 = | 0.27676 | tm
34
35 | B. REINFORCEMENTS
36 | -ve Mu/bd2 at support across long span |  | = 1.5*0.61*10000/120^2 = |  | 0.63589 | N/mm2
37 | +ve Mu/bd2 at mid span across long span |  | = 1.5*0.46*10000/120^2 = |  | 0.48103 | N/mm2
38 | -ve Mu/bd2 at support across short span |  | = 1.5*0.37*10000/120^2 = |  | 0.38096 | N/mm2
39 | +ve Mu/bd2 at mid span across short span |  | = 1.5*0.28*10000/120^2 = |  | 0.28829 | N/mm2
40
41 | Max. Mu/bd2 |  |  | Max. of (0.64:0.29) | 0.63589 | N/mm2
44 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
45 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
46
47 |  |  | Reinf as per Table-2,Pg-48,SP-16
48 | Reqd. reinf | Mu/bd2 | ptxd/10
49
50 | For -ve moment i.e. top reinf. across long span | 0.63589 | 0.1492 | = 0.149*12/10 = | 1.7904 | cm2/m
51 | For +ve moment i.e. bottom reinf. across long span | 0.48103 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
52 | For -ve moment i.e. top reinf. across short span | 0.38096 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
53 | For +ve moment i.e. bottom reinf. across short span | 0.28829 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
54
55 | Main Reinforcements | F | spacing
56 | At top across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
57 | At bottom across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
58 | At top across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
59 | At bottom across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
60 |  |  |  |  | Max. % steel = |  | 0.168
62 | Max. permissible spacing | 3 | 360 | (As per Cl. 26.3.3; Pg. 46; IS:456)
63 |  | or | 300
64 | Least of the two |  | 300
65 | Max. provided spacing |  | 250
66 |  |  | OK
68 | Distribution Reinforcement
69 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
70 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
71 | Provide | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m
72 | Max. permissible spacing | 5 | 600 | (As per Cl. 26.3.3; Pg. 46; IS:456)
73 |  | or | 450
74 | Least of the two |  | 450
75 | Max. provided spacing |  | 250
76 |  |  | OK
78 | C. DEFLECTION CHECK
79 | Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
80 |  |  |  | Cantilever | 7
81 |  |  |  | Simply supported | 20
82 |  |  |  | Continuous | 26
83 | fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 258.133
| Multiplication factor corresponding to steel service stress of 0.168% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 1.7482
84 | Modified applicable ratio assuming 'Discontinuous' |  |  | = 1.75*26 = | 45.454
85 | Actual 'Span' to 'Depth' ratio |  |  | = 2750/120 = | 22.9167
86 |  | OK from deflection considerations.
87
88 | D. SKETCH
89
90 |  |  |  | 8 | 250
91
92 |  |  | 8 | 250
93
94 | 2750
95 |  |  |  |  | 8 | 250
96 |  |  | 8 | 250
97
98
99 |  | 4660
100 |  |  | PLAN
101
102 |  | All distribution rebars = | 8 | 250
103
104
105 | [5 empty] | 150
106
107
108 |  |  | SECTION
109
110 | Provided rebars on drawings may be the same or greater than the above design requirements.
111
112
113
114
115

## S26 (hidden)
STRUCTURE : |  | ADMIN BUILDING
ITEM : |  | SLAB, S26 | [5 empty] | 1 | 1 Interior panel
Sl. No. | ITEM | NOTN. | FORMULA | CALCULATIONS | VALUE | UNIT | REMARKS | 2 | 2 one short edge disc.
[8 empty] | 3 | 3 one long edge disc.
A | B | C | D | E | F | G | H | 4 | 4 Two adjacent edge disc.
A: 1; B: Longer clear span; D: =; F: 4635 | 5 | 5 Two short edge disc.
[8 empty] | 6 | 6 Two long. edge disc.
A: 2; B: Sorter clear span; D: =; F: 2750 | 7 | 7 Three edge disc.(one Long edge cont.)
[8 empty] | 8 | 8 Three edge disc.(one short edge cont.)
A: 3; B: Thickness of Slab; D: =; F: 150 | 9 | 9 Four edge disc.
[10 empty] | 1 | 1 | Interior panel
A: 4; B: Total UDL.; D: =; F: 1.2 |  |  | 2 | 2 | one short edge disc.
[10 empty] | 3 | 3 | one long edge disc.
A: 5; B: Support Condition; D: =; F: 1 Interior panel |  |  | 4 | 4 | Two adjacent edge disc.
[10 empty] | 5 | 5 | Two short edge disc.
A: 8; B: A. DESIGN FORCES |  |  | 7 | 7 | Three edge disc.(one Long edge cont.)
9 | Longer clear span |  |  |  | 4635 | <mm; m> | 4.635 |  |  | 7 | 7 | Three edge disc.(one short edge cont.)
10 | Sorter clear span |  |  |  | 2750 | <mm; m> | 2.75 |  |  | 8 | 8 | Four edge disc.
11
12 | Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 150 | <mm; m> | 0.15
| Clear cover to main reinf |  |  |  | 25 | mm
| Maximum diameter of bar |  |  |  | 10 | mm
| Facor of safety |  |  |  | 1.5 | mm
| minimum slab thkness |  |  |  | 110 | mm
| Permissible Mu/bd2 |  |  |  | 2.76
13 |  | OK,More than the min. as per tender.
14 |  | OK, From max. Mu/bd2 considerations as detailed hereunder.
15 |  | OK from deflection considerations as checked hereunder.
16 | The least effective depth in shorter / longer direction |  |  | = 150-25 -10/2 = | 120 | <mm; cm> | 12
17
| Total design UDL |  |  |  | 1.2 | t/m2
19 |  |  |  | Say | 1.2 | t/m2
21
22 | Longer effective span | LY |  | = 4635+120 = | 4755 | <mm; m> | 4.755
23 | Sorter effective span | Lx |  | = 2750+120 = | 2870 | <mm; m> | 2.87
24 |  |  | Ly/Lx | = 4755/2870 = | 1.66
26
27 | Shorter of the two spans (for use in bending moment calculations) |  |  |  | 2870 | <mm; m> | 2.87
28
29 | Refering IS-456, Table-22, P91 |  | 1 | 1 Interior panel
30 | -ve support moment at continuous edge across long span | -My | 0.05748 | = 0.057*1.2*2.87^2 = | 0.56815 | tm
31 | +ve moment at mid span across long span | +My | 0.04356 | = 0.044*1.2*2.87^2 = | 0.43056 | tm
32 | -ve support moment at continuous edge across short span | -Mx | 0.032 | = 0.032*1.2*2.87^2 = | 0.3163 | tm
33 | +ve moment at mid span across short span | +Mx | 0.024 | = 0.024*1.2*2.87^2 = | 0.23722 | tm
34
35 | B. REINFORCEMENTS
36 | -ve Mu/bd2 at support across long span |  | = 1.5*0.57*10000/120^2 = |  | 0.59182 | N/mm2
37 | +ve Mu/bd2 at mid span across long span |  | = 1.5*0.43*10000/120^2 = |  | 0.4485 | N/mm2
38 | -ve Mu/bd2 at support across short span |  | = 1.5*0.32*10000/120^2 = |  | 0.32948 | N/mm2
39 | +ve Mu/bd2 at mid span across short span |  | = 1.5*0.24*10000/120^2 = |  | 0.24711 | N/mm2
40
41 | Max. Mu/bd2 |  |  | Max. of (0.59:0.25) | 0.59182 | N/mm2
44 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
45 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
46
47 |  |  | Reinf as per Table-2,Pg-48,SP-16
48 | Reqd. reinf | Mu/bd2 | ptxd/10
49
50 | For -ve moment i.e. top reinf. across long span | 0.59182 | 0.1396 | = 0.14*12/10 = | 1.6752 | cm2/m
51 | For +ve moment i.e. bottom reinf. across long span | 0.4485 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
52 | For -ve moment i.e. top reinf. across short span | 0.32948 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
53 | For +ve moment i.e. bottom reinf. across short span | 0.24711 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
54
55 | Main Reinforcements | F | spacing
56 | At top across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
57 | At bottom across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
58 | At top across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
59 | At bottom across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
60 |  |  |  |  | Max. % steel = |  | 0.168
62 | Max. permissible spacing | 3 | 360 | (As per Cl. 26.3.3; Pg. 46; IS:456)
63 |  | or | 300
64 | Least of the two |  | 300
65 | Max. provided spacing |  | 250
66 |  |  | OK
68 | Distribution Reinforcement
69 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
70 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
71 | Provide | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m
72 | Max. permissible spacing | 5 | 600 | (As per Cl. 26.3.3; Pg. 46; IS:456)
73 |  | or | 450
74 | Least of the two |  | 450
75 | Max. provided spacing |  | 250
76 |  |  | OK
78 | C. DEFLECTION CHECK
79 | Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
80 |  |  |  | Cantilever | 7
81 |  |  |  | Simply supported | 20
82 |  |  |  | Continuous | 26
83 | fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 241.5239
| Multiplication factor corresponding to steel service stress of 0.168% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 1.9285
84 | Modified applicable ratio assuming 'Discontinuous' |  |  | = 1.93*26 = | 50.1422
85 | Actual 'Span' to 'Depth' ratio |  |  | = 2750/120 = | 22.9167
86 |  | OK from deflection considerations.
87
88 | D. SKETCH
89
90 |  |  |  | 8 | 250
91
92 |  |  | 8 | 250
93
94 | 2750
95 |  |  |  |  | 8 | 250
96 |  |  | 8 | 250
97
98
99 |  | 4635
100 |  |  | PLAN
101
102 |  | All distribution rebars = | 8 | 250
103
104
105 | [5 empty] | 150
106
107
108 |  |  | SECTION
109
110 | Provided rebars on drawings may be the same or greater than the above design requirements.
111
112
113
114
115

## S27 (hidden)
Slab-S27
CALCULATION OF B.M IN SLAB
|  |  |  | 0.078 |  | 0.102 | Wl2
0.046
[5 empty] | 0.078 | *Wl2
| l = | 1.5 | M
|  |  |  | w | = | 1.2 | t/sqm
Moment at ist Support |  |  | = | 0.2754 | t-m/m
Moment at 1st Span |  |  | = | 0.2106 | t-m/m
Moment at int Support |  |  | = | 0.2106 | t-m/m
Moment at int Span |  |  | = | 0.1242 | t-m/m
|  | Depth of slab | = | 150 | mm
|  | Effective Depth | = | 125 | mm
|  | Yield Stress of Reinf |  | 500 | n/mm2
Reinf as per Table-3,Pg-49,SP-16
| Reqd. reinf | Mu/bd2 | ptxd/10 |  | Reqd |  | %of Reinf
For -ve moment i.e. top reinf. 1st supp |  | 0.26438 | 0.12 | (0.12*1000*125)/100) | 150 | cm2/m | 0.12
For +ve moment 1st span |  | 0.20218 | 0.12 | (0.12*1000*)/100) | 150 | cm2/m | 0.12
For -ve moment i.e. top reinf. int supp |  | 0.20218 | 0.12 | (0.12*1000*)/100) | 150 | cm2/m | 0.12
For +ve moment int span |  | 0.11923 | 0.12 | (0.12*1000*)/100) | 150 | cm2/m | 0.12
| Main Reinforcements | F | spacing
For -ve moment i.e. top reinf. 1st supp |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
For +ve moment 1st span |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
For -ve moment i.e. top reinf. int supp |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
For +ve moment intspan |  | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 201.1429 | cm2/m | 0.16091 | TRUE
0.16091
C. DEFLECTION CHECK
| Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
|  |  |  | Cantilever | 7
|  |  |  | Simply supported | 20
|  |  |  | Continuous | 26
| fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 216.264
| Multiplication factor corresponding to steel service stress of 0.161% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 2
| Modified applicable ratio assuming 'Discontinuous' |  |  | = 26*2 = | 52
| Actual 'Span' to 'Depth' ratio |  |  | = 1500/125 = | 12
OK from deflection considerations.

## slab at pi (hidden)
Slab-at pipe inlet level
CALCULATION OF B.M IN SLAB
|  |  |  | 0.078 |  | 0.102 | Wl2
0.046
[5 empty] | 0.078 | *Wl2
| l = | 0.8 | M
|  |  |  | w | = | 1 | t/sqm
Moment at ist Support |  |  | = | 0.06528 | t-m/m
Moment at 1st Span |  |  | = | 0.04992 | t-m/m
Moment at int Support |  |  | = | 0.04992 | t-m/m
Moment at int Span |  |  | = | 0.02944 | t-m/m
[9 empty] | thickness |  | 200
For Servicibility
DESIGN DATA
|  | Clear cover to reinf | [7 empty] | 50 | mm
|  | Effective cover | [7 empty] | 60 | mm
|  | Sigmast on water face face |  |  |  | FY | 500 |  | (0.8*500) | 400 | N/mm2
|  | Sigmast on earth face face | [7 empty] | 250 | N/mm2
|  | fck | [7 empty] | 30 | N/mm2
|  | σcbc | [7 empty] | 10 | N/mm2
|  | m | 2*Es/Ec | [6 empty] | 14.61
|  | Es | [7 empty] | 200000 | N/mm2 | 200000
| M | Moment at h3 from top | [7 empty] | 0.06528 | T-M/M | 0.06528
|  |  |  | / | 1000
| b | B = WIDTH | 1000 | [6 empty] | 1000 | mm | 1000
| h | D =DEPTH | 200 | [6 empty] | 200 | mm | 200
|  | CLEAR COVER |  | 60 | [5 empty] | 60 | mm | 60
| d | d =EFF.DEPTH | (200-60) | [6 empty] | 140 | mm | 140
| σst | [8 empty] | 400 | N/mm2 | 400
| Ast =(1-SQRT(1-((4.6*Mu)/(fck*b*d^2))))/((2/(b*d))*(fy/fck)) | AST =AREA OF STEEL | ((1-SQRT(1-((4.6*0.06528*1.5*10^7)/(30*1000*140^2))))/((2/(1000*140))*(500/30))) | [6 empty] | 16.12 | mm2 | 16.12
| Y= d*Ast/b/d*m (sqrt(1+2/ Ast/b/d*m) -1 ) | Y =DPTH OF N.A | (140*((14.61*(392.5/1000/140))*((1+2/(392.5/1000/140)^0.5)-1))) | [6 empty] | 34.744 | mm | 34.744
| Z = d-y/3 |  | (140-34.744/3) | [6 empty] | 128.42 | mm | 128.42
| fs = Tensile stress in steel in service condition = Ms/Z*As |  | (0.06528*10^7/128.42/392.5) | [6 empty] | 12.95 | N/mm2 | 12.95 | ok
| fcb = Compressive stress in Concrete in service condition = 2*Ms/Z*b*y |  | (2*0.06528*10^7/128.42/1000/34.744) | [6 empty] | 0.29262 | N/mm2 | 0.29262 | ok
| ε1 =( (h-y)*fs)/((d-y)*Es) | Average elastic tensile strai in concrete | ((200-34.744)*12.95/(140-34.744)/200000) | [6 empty] | 0.00010166 |  | 0.00010166
| ε2 =1.0*b*(h-y)*(h-y)/(3*Es*As*(d-y)) |  | ((1.0*1000*(200-34.744)^2)/(3*200000*392.5*(140-34.744))) | [6 empty] | 0.0011017 |  | 0.0016526
| εm = ε1-ε2 |  | (200)*(1000)+(10*16.12) | [6 empty] | -0.001 |  | -0.00155
| acr | SIGCBCALL= | 111.62 | [6 empty] | 111.62 |  | 111.62
| w = (3*acr*em)/(1+2(acr-cmin)/(h-x)) | Crck Width | (3*111.62*-0.00155)/(1+(2*(111.62-(60-10))/(200-34.744))) | [7 empty] | OK | -0.29731
|  | Ast Reqd | [6 empty] | ALLOWABLE CRACK WIDTH |  | 0.2
|  | 16.12 | 10 | @ | 200 | 392.5
|  |  | 0 | @ | 400 | 0
|  |  | 0 | @ | 400 | 0
|  |  | 0 | @ | 400 | 0
392.5
|  |  | net spacing |  | 200 | OK |  | MORE THAN MINIMUM
| minimum reinf | 0.175 |  |  |  | 350

## slab at 114.76 (hidden)
Slab-at ffl
CALCULATION OF B.M IN SLAB
|  |  |  | 0.078 |  | 0.102 | Wl2
0.046
[5 empty] | 0.078 | *Wl2
| l = | 3.25 | M
|  |  |  | w | = | 1 | t/sqm
Moment at ist Support |  |  | = | 1.0774 | t-m/m
Moment at 1st Span |  |  | = | 0.82388 | t-m/m
.
Moment at int Support |  |  | = | 0.82388 | t-m/m
Moment at int Span |  |  | = | 0.48588 | t-m/m
|  | Depth of slab | = | 150 | mm
|  | Effective Depth | = | 125 | mm
|  | Yield Stress of Reinf |  | 500 | n/mm2
Reinf as per Table-3,Pg-49,SP-16
| Reqd. reinf | Mu/bd2 | ptxd/10 |  | Reqd |  | %of Reinf
For -ve moment i.e. top reinf. 1st supp |  | 1.0343 | 0.291 | (0.291*1000*125)/100) | 363.75 | cm2/m | 0.291
For +ve moment 1st span |  | 0.79092 | 0.216 | (0.216*1000*)/100) | 270 | cm2/m | 0.216
For -ve moment i.e. top reinf. int supp |  | 0.79092 | 0.216 | (0.216*1000*)/100) | 270 | cm2/m | 0.216
For +ve moment int span |  | 0.46644 | 0.127 | (0.127*1000*)/100) | 158.75 | cm2/m | 0.127
| Main Reinforcements | F | spacing
For -ve moment i.e. top reinf. 1st supp |  | 8 | 100 | = pi/4*(8/10)^2*1000/100 = | 502.8571 | cm2/m | 0.40229 | TRUE
For +ve moment 1st span |  | 8 | 100 | = pi/4*(8/10)^2*1000/100 = | 502.8571 | cm2/m | 0.40229 | TRUE
For -ve moment i.e. top reinf. int supp |  | 8 | 100 | = pi/4*(8/10)^2*1000/100 = | 502.8571 | cm2/m | 0.40229 | TRUE
For +ve moment intspan |  | 8 | 100 | = pi/4*(8/10)^2*1000/100 = | 502.8571 | cm2/m | 0.40229 | TRUE
0.40229
C. DEFLECTION CHECK
| Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
|  |  |  | Cantilever | 7
|  |  |  | Simply supported | 20
|  |  |  | Continuous | 26
| fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 209.776
| Multiplication factor corresponding to steel service stress of 0.402% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 1.5307
| Modified applicable ratio assuming 'Discontinuous' |  |  | = 26*1.53 = | 39.7972
| Actual 'Span' to 'Depth' ratio |  |  | = 3250/125 = | 26
OK from deflection considerations.

## S29 (hidden)
STRUCTURE : |  | ADMIN BUILDING
ITEM : |  | SLAB, S29 | [5 empty] | 1 | 1 Interior panel
Sl. No. | ITEM | NOTN. | FORMULA | CALCULATIONS | VALUE | UNIT | REMARKS | 2 | 2 one short edge disc.
[8 empty] | 3 | 3 one long edge disc.
A | B | C | D | E | F | G | H | 4 | 4 Two adjacent edge disc.
A: 1; B: Longer clear span; D: =; F: 4635 | 5 | 5 Two short edge disc.
[8 empty] | 6 | 6 Two long. edge disc.
A: 2; B: Sorter clear span; D: =; F: 2750 | 7 | 7 Three edge disc.(one Long edge cont.)
[8 empty] | 8 | 8 Three edge disc.(one short edge cont.)
A: 3; B: Thickness of Slab; D: =; F: 150 | 9 | 9 Four edge disc.
[10 empty] | 1 | 1 | Interior panel
A: 4; B: Total UDL.; D: =; F: 1.2 |  |  | 2 | 2 | one short edge disc.
[10 empty] | 3 | 3 | one long edge disc.
A: 5; B: Support Condition; D: =; F: 1 Interior panel |  |  | 4 | 4 | Two adjacent edge disc.
[10 empty] | 5 | 5 | Two short edge disc.
A: 8; B: A. DESIGN FORCES |  |  | 7 | 7 | Three edge disc.(one Long edge cont.)
9 | Longer clear span |  |  |  | 4635 | <mm; m> | 4.635 |  |  | 7 | 7 | Three edge disc.(one short edge cont.)
10 | Sorter clear span |  |  |  | 2750 | <mm; m> | 2.75 |  |  | 8 | 8 | Four edge disc.
11
12 | Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 150 | <mm; m> | 0.15
| Clear cover to main reinf |  |  |  | 25 | mm
| Maximum diameter of bar |  |  |  | 10 | mm
| Facor of safety |  |  |  | 1.5 | mm
| minimum slab thkness |  |  |  | 110 | mm
| Permissible Mu/bd2 |  |  |  | 2.76
13 |  | OK,More than the min. as per tender.
14 |  | OK, From max. Mu/bd2 considerations as detailed hereunder.
15 |  | OK from deflection considerations as checked hereunder.
16 | The least effective depth in shorter / longer direction |  |  | = 150-25 -10/2 = | 120 | <mm; cm> | 12
17
| Total design UDL |  |  |  | 1.2 | t/m2
19 |  |  |  | Say | 1.2 | t/m2
21
22 | Longer effective span | LY |  | = 4635+120 = | 4755 | <mm; m> | 4.755
23 | Sorter effective span | Lx |  | = 2750+120 = | 2870 | <mm; m> | 2.87
24 |  |  | Ly/Lx | = 4755/2870 = | 1.66
26
27 | Shorter of the two spans (for use in bending moment calculations) |  |  |  | 2870 | <mm; m> | 2.87
28
29 | Refering IS-456, Table-22, P91 |  | 1 | 1 Interior panel
30 | -ve support moment at continuous edge across long span | -My | 0.05748 | = 0.057*1.2*2.87^2 = | 0.56815 | tm
31 | +ve moment at mid span across long span | +My | 0.04356 | = 0.044*1.2*2.87^2 = | 0.43056 | tm
32 | -ve support moment at continuous edge across short span | -Mx | 0.032 | = 0.032*1.2*2.87^2 = | 0.3163 | tm
33 | +ve moment at mid span across short span | +Mx | 0.024 | = 0.024*1.2*2.87^2 = | 0.23722 | tm
34
35 | B. REINFORCEMENTS
36 | -ve Mu/bd2 at support across long span |  | = 1.5*0.57*10000/120^2 = |  | 0.59182 | N/mm2
37 | +ve Mu/bd2 at mid span across long span |  | = 1.5*0.43*10000/120^2 = |  | 0.4485 | N/mm2
38 | -ve Mu/bd2 at support across short span |  | = 1.5*0.32*10000/120^2 = |  | 0.32948 | N/mm2
39 | +ve Mu/bd2 at mid span across short span |  | = 1.5*0.24*10000/120^2 = |  | 0.24711 | N/mm2
40
41 | Max. Mu/bd2 |  |  | Max. of (0.59:0.25) | 0.59182 | N/mm2
44 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
45 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
46
47 |  |  | Reinf as per Table-2,Pg-48,SP-16
48 | Reqd. reinf | Mu/bd2 | ptxd/10
49
50 | For -ve moment i.e. top reinf. across long span | 0.59182 | 0.1396 | = 0.14*12/10 = | 1.6752 | cm2/m
51 | For +ve moment i.e. bottom reinf. across long span | 0.4485 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
52 | For -ve moment i.e. top reinf. across short span | 0.32948 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
53 | For +ve moment i.e. bottom reinf. across short span | 0.24711 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
54
55 | Main Reinforcements | F | spacing
56 | At top across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
57 | At bottom across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
58 | At top across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
59 | At bottom across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
60 |  |  |  |  | Max. % steel = |  | 0.168
62 | Max. permissible spacing | 3 | 360 | (As per Cl. 26.3.3; Pg. 46; IS:456)
63 |  | or | 300
64 | Least of the two |  | 300
65 | Max. provided spacing |  | 250
66 |  |  | OK
68 | Distribution Reinforcement
69 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
70 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
71 | Provide | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m
72 | Max. permissible spacing | 5 | 600 | (As per Cl. 26.3.3; Pg. 46; IS:456)
73 |  | or | 450
74 | Least of the two |  | 450
75 | Max. provided spacing |  | 250
76 |  |  | OK
78 | C. DEFLECTION CHECK
79 | Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
80 |  |  |  | Cantilever | 7
81 |  |  |  | Simply supported | 20
82 |  |  |  | Continuous | 26
83 | fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 241.5239
| Multiplication factor corresponding to steel service stress of 0.168% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 1.9285
84 | Modified applicable ratio assuming 'Discontinuous' |  |  | = 1.93*26 = | 50.1422
85 | Actual 'Span' to 'Depth' ratio |  |  | = 2750/120 = | 22.9167
86 |  | OK from deflection considerations.
87
88 | D. SKETCH
89
90 |  |  |  | 8 | 250
91
92 |  |  | 8 | 250
93
94 | 2750
95 |  |  |  |  | 8 | 250
96 |  |  | 8 | 250
97
98
99 |  | 4635
100 |  |  | PLAN
101
102 |  | All distribution rebars = | 8 | 250
103
104
105 | [5 empty] | 150
106
107
108 |  |  | SECTION
109
110 | Provided rebars on drawings may be the same or greater than the above design requirements.
111
112
113
114
115

## S30 (hidden)
STRUCTURE : |  | ADMIN BUILDING
ITEM : |  | SLAB, S30 | [5 empty] | 1 | 1 Interior panel
Sl. No. | ITEM | NOTN. | FORMULA | CALCULATIONS | VALUE | UNIT | REMARKS | 2 | 2 one short edge disc.
[8 empty] | 3 | 3 one long edge disc.
A | B | C | D | E | F | G | H | 4 | 4 Two adjacent edge disc.
A: 1; B: Longer clear span; D: =; F: 4660 | 5 | 5 Two short edge disc.
[8 empty] | 6 | 6 Two long. edge disc.
A: 2; B: Sorter clear span; D: =; F: 2750 | 7 | 7 Three edge disc.(one Long edge cont.)
[8 empty] | 8 | 8 Three edge disc.(one short edge cont.)
A: 3; B: Thickness of Slab; D: =; F: 150 | 9 | 9 Four edge disc.
[10 empty] | 1 | 1 | Interior panel
A: 4; B: Total UDL.; D: =; F: 1.2 |  |  | 2 | 2 | one short edge disc.
[10 empty] | 3 | 3 | one long edge disc.
A: 5; B: Support Condition; D: =; F: 4 Two adjacent edge disc. |  |  | 4 | 4 | Two adjacent edge disc.
[10 empty] | 5 | 5 | Two short edge disc.
A: 8; B: A. DESIGN FORCES |  |  | 7 | 7 | Three edge disc.(one Long edge cont.)
9 | Longer clear span |  |  |  | 4660 | <mm; m> | 4.66 |  |  | 7 | 7 | Three edge disc.(one short edge cont.)
10 | Sorter clear span |  |  |  | 2750 | <mm; m> | 2.75 |  |  | 8 | 8 | Four edge disc.
11
12 | Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 150 | <mm; m> | 0.15
| Clear cover to main reinf |  |  |  | 25 | mm
| Maximum diameter of bar |  |  |  | 10 | mm
| Facor of safety |  |  |  | 1.5 | mm
| minimum slab thkness |  |  |  | 110 | mm
| Permissible Mu/bd2 |  |  |  | 2.76
13 |  | OK,More than the min. as per tender.
14 |  | OK, From max. Mu/bd2 considerations as detailed hereunder.
15 |  | OK from deflection considerations as checked hereunder.
16 | The least effective depth in shorter / longer direction |  |  | = 150-25 -10/2 = | 120 | <mm; cm> | 12
17
| Total design UDL |  |  |  | 1.2 | t/m2
19 |  |  |  | Say | 1.2 | t/m2
21
22 | Longer effective span | LY |  | = 4660+120 = | 4780 | <mm; m> | 4.78
23 | Sorter effective span | Lx |  | = 2750+120 = | 2870 | <mm; m> | 2.87
24 |  |  | Ly/Lx | = 4780/2870 = | 1.67
26
27 | Shorter of the two spans (for use in bending moment calculations) |  |  |  | 2870 | <mm; m> | 2.87
28
29 | Refering IS-456, Table-22, P91 |  | 4 | 4 Two adjacent edge disc.
30 | -ve support moment at continuous edge across long span | -My | 0.08112 | = 0.081*1.2*2.87^2 = | 0.80181 | tm
31 | +ve moment at mid span across long span | +My | 0.06076 | = 0.061*1.2*2.87^2 = | 0.60057 | tm
32 | -ve support moment at continuous edge across short span | -Mx | 0.047 | = 0.047*1.2*2.87^2 = | 0.46456 | tm
33 | +ve moment at mid span across short span | +Mx | 0.035 | = 0.035*1.2*2.87^2 = | 0.34595 | tm
34
35 | B. REINFORCEMENTS
36 | -ve Mu/bd2 at support across long span |  | = 1.5*0.8*10000/120^2 = |  | 0.83522 | N/mm2
37 | +ve Mu/bd2 at mid span across long span |  | = 1.5*0.6*10000/120^2 = |  | 0.62559 | N/mm2
38 | -ve Mu/bd2 at support across short span |  | = 1.5*0.46*10000/120^2 = |  | 0.48392 | N/mm2
39 | +ve Mu/bd2 at mid span across short span |  | = 1.5*0.35*10000/120^2 = |  | 0.36036 | N/mm2
40
41 | Max. Mu/bd2 |  |  | Max. of (0.84:0.36) | 0.83522 | N/mm2
44 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
45 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
46
47 |  |  | Reinf as per Table-2,Pg-48,SP-16
48 | Reqd. reinf | Mu/bd2 | ptxd/10
49
50 | For -ve moment i.e. top reinf. across long span | 0.83522 | 0.1988 | = 0.199*12/10 = | 2.3856 | cm2/m
51 | For +ve moment i.e. bottom reinf. across long span | 0.62559 | 0.1468 | = 0.147*12/10 = | 1.7616 | cm2/m
52 | For -ve moment i.e. top reinf. across short span | 0.48392 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
53 | For +ve moment i.e. bottom reinf. across short span | 0.36036 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
54
55 | Main Reinforcements | F | spacing
56 | At top across long span | 8 | 200 | = pi/4*(8/10)^2*1000/200 = | 2.5143 | cm2/m | 0.21
57 | At bottom across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
58 | At top across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
59 | At bottom across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
60 |  |  |  |  | Max. % steel = |  | 0.21
62 | Max. permissible spacing | 3 | 360 | (As per Cl. 26.3.3; Pg. 46; IS:456)
63 |  | or | 300
64 | Least of the two |  | 300
65 | Max. provided spacing |  | 250
66 |  |  | OK
68 | Distribution Reinforcement
69 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
70 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
71 | Provide | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m
72 | Max. permissible spacing | 5 | 600 | (As per Cl. 26.3.3; Pg. 46; IS:456)
73 |  | or | 450
74 | Least of the two |  | 450
75 | Max. provided spacing |  | 250
76 |  |  | OK
78 | C. DEFLECTION CHECK
79 | Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
80 |  |  |  | Cantilever | 7
81 |  |  |  | Simply supported | 20
82 |  |  |  | Continuous | 26
83 | fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 275.1573
| Multiplication factor corresponding to steel service stress of 0.21% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 1.4548
84 | Modified applicable ratio assuming 'Discontinuous' |  |  | = 1.45*26 = | 37.824
85 | Actual 'Span' to 'Depth' ratio |  |  | = 2750/120 = | 22.9167
86 |  | OK from deflection considerations.
87
88 | D. SKETCH
89
90 |  |  |  | 8 | 200
91
92 |  |  | 8 | 250
93
94 | 2750
95 |  |  |  |  | 8 | 250
96 |  |  | 8 | 250
97
98
99 |  | 4660
100 |  |  | PLAN
101
102 |  | All distribution rebars = | 8 | 250
103
104
105 | [5 empty] | 150
106
107
108 |  |  | SECTION
109
110 | Provided rebars on drawings may be the same or greater than the above design requirements.
111
112
113
114
115

## S31 (hidden)
STRUCTURE : |  | ADMIN BUILDING
ITEM : |  | SLAB, S31 | [5 empty] | 1 | 1 Interior panel
Sl. No. | ITEM | NOTN. | FORMULA | CALCULATIONS | VALUE | UNIT | REMARKS | 2 | 2 one short edge disc.
[8 empty] | 3 | 3 one long edge disc.
A | B | C | D | E | F | G | H | 4 | 4 Two adjacent edge disc.
A: 1; B: Longer clear span; D: =; F: 4635 | 5 | 5 Two short edge disc.
[8 empty] | 6 | 6 Two long. edge disc.
A: 2; B: Sorter clear span; D: =; F: 2750 | 7 | 7 Three edge disc.(one Long edge cont.)
[8 empty] | 8 | 8 Three edge disc.(one short edge cont.)
A: 3; B: Thickness of Slab; D: =; F: 150 | 9 | 9 Four edge disc.
[10 empty] | 1 | 1 | Interior panel
A: 4; B: Total UDL.; D: =; F: 1.2 |  |  | 2 | 2 | one short edge disc.
[10 empty] | 3 | 3 | one long edge disc.
A: 5; B: Support Condition; D: =; F: 3 one long edge disc. |  |  | 4 | 4 | Two adjacent edge disc.
[10 empty] | 5 | 5 | Two short edge disc.
A: 8; B: A. DESIGN FORCES |  |  | 7 | 7 | Three edge disc.(one Long edge cont.)
9 | Longer clear span |  |  |  | 4635 | <mm; m> | 4.635 |  |  | 7 | 7 | Three edge disc.(one short edge cont.)
10 | Sorter clear span |  |  |  | 2750 | <mm; m> | 2.75 |  |  | 8 | 8 | Four edge disc.
11
12 | Assumed thickness of slab | t | (By trial & error till OK for various requirements as analysed hereunder.) |  | 150 | <mm; m> | 0.15
| Clear cover to main reinf |  |  |  | 25 | mm
| Maximum diameter of bar |  |  |  | 10 | mm
| Facor of safety |  |  |  | 1.5 | mm
| minimum slab thkness |  |  |  | 110 | mm
| Permissible Mu/bd2 |  |  |  | 2.76
13 |  | OK,More than the min. as per tender.
14 |  | OK, From max. Mu/bd2 considerations as detailed hereunder.
15 |  | OK from deflection considerations as checked hereunder.
16 | The least effective depth in shorter / longer direction |  |  | = 150-25 -10/2 = | 120 | <mm; cm> | 12
17
| Total design UDL |  |  |  | 1.2 | t/m2
19 |  |  |  | Say | 1.2 | t/m2
21
22 | Longer effective span | LY |  | = 4635+120 = | 4755 | <mm; m> | 4.755
23 | Sorter effective span | Lx |  | = 2750+120 = | 2870 | <mm; m> | 2.87
24 |  |  | Ly/Lx | = 4755/2870 = | 1.66
26
27 | Shorter of the two spans (for use in bending moment calculations) |  |  |  | 2870 | <mm; m> | 2.87
28
29 | Refering IS-456, Table-22, P91 |  | 3 | 3 one long edge disc.
30 | -ve support moment at continuous edge across long span | -My | 0.0734 | = 0.073*1.2*2.87^2 = | 0.72551 | tm
31 | +ve moment at mid span across long span | +My | 0.05612 | = 0.056*1.2*2.87^2 = | 0.55471 | tm
32 | -ve support moment at continuous edge across short span | -Mx | 0.037 | = 0.037*1.2*2.87^2 = | 0.36572 | tm
33 | +ve moment at mid span across short span | +Mx | 0.028 | = 0.028*1.2*2.87^2 = | 0.27676 | tm
34
35 | B. REINFORCEMENTS
36 | -ve Mu/bd2 at support across long span |  | = 1.5*0.73*10000/120^2 = |  | 0.75574 | N/mm2
37 | +ve Mu/bd2 at mid span across long span |  | = 1.5*0.55*10000/120^2 = |  | 0.57782 | N/mm2
38 | -ve Mu/bd2 at support across short span |  | = 1.5*0.37*10000/120^2 = |  | 0.38096 | N/mm2
39 | +ve Mu/bd2 at mid span across short span |  | = 1.5*0.28*10000/120^2 = |  | 0.28829 | N/mm2
40
41 | Max. Mu/bd2 |  |  | Max. of (0.76:0.29) | 0.75574 | N/mm2
44 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
45 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
46
47 |  |  | Reinf as per Table-2,Pg-48,SP-16
48 | Reqd. reinf | Mu/bd2 | ptxd/10
49
50 | For -ve moment i.e. top reinf. across long span | 0.75574 | 0.179 | = 0.179*12/10 = | 2.148 | cm2/m
51 | For +ve moment i.e. bottom reinf. across long span | 0.57782 | 0.1348 | = 0.135*12/10 = | 1.6176 | cm2/m
52 | For -ve moment i.e. top reinf. across short span | 0.38096 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
53 | For +ve moment i.e. bottom reinf. across short span | 0.28829 | 0.12 | = 0.12*12/10 = | 1.44 | cm2/m
54
55 | Main Reinforcements | F | spacing
56 | At top across long span | 8 | 220 | = pi/4*(8/10)^2*1000/220 = | 2.2857 | cm2/m | 0.19
57 | At bottom across long span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
58 | At top across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
59 | At bottom across short span | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m | 0.168
60 |  |  |  |  | Max. % steel = |  | 0.19
62 | Max. permissible spacing | 3 | 360 | (As per Cl. 26.3.3; Pg. 46; IS:456)
63 |  | or | 300
64 | Least of the two |  | 300
65 | Max. provided spacing |  | 250
66 |  |  | OK
68 | Distribution Reinforcement
69 | Min. reinf. in each direction - as per Cl. 26.5.2.1; Pg. 48; IS:456
70 | 0.12 |  |  | = 0.0012*12*100 = | 1.44 | cm2/m
71 | Provide | 8 | 250 | = pi/4*(8/10)^2*1000/250 = | 2.0114 | cm2/m
72 | Max. permissible spacing | 5 | 600 | (As per Cl. 26.3.3; Pg. 46; IS:456)
73 |  | or | 450
74 | Least of the two |  | 450
75 | Max. provided spacing |  | 250
76 |  |  | OK
78 | C. DEFLECTION CHECK
79 | Permissible 'Span' to 'Depth' ratio |  | (As per Cl. 23.2.1; Pg. 37; IS:456)
80 |  |  |  | Cantilever | 7
81 |  |  |  | Simply supported | 20
82 |  |  |  | Continuous | 26
83 | fs = 0.58*Ast Reqd/Ast Pro |  |  |  | 272.5275
| Multiplication factor corresponding to steel service stress of 0.19% steel from Fig. 4, Pg. 38; IS:456 |  |  |  | 1.5343
84 | Modified applicable ratio assuming 'Discontinuous' |  |  | = 1.53*26 = | 39.892
85 | Actual 'Span' to 'Depth' ratio |  |  | = 2750/120 = | 22.9167
86 |  | OK from deflection considerations.
87
88 | D. SKETCH
89
90 |  |  |  | 8 | 220
91
92 |  |  | 8 | 250
93
94 | 2750
95 |  |  |  |  | 8 | 250
96 |  |  | 8 | 250
97
98
99 |  | 4635
100 |  |  | PLAN
101
102 |  | All distribution rebars = | 8 | 250
103
104
105 | [5 empty] | 150
106
107
108 |  |  | SECTION
109
110 | Provided rebars on drawings may be the same or greater than the above design requirements.
111
112
113
114
115

## Sheet1 (hidden)
DEAD LOAD | Typical floor slab | 0.7 | Typical floor slab | 0.75
| Additional load in Auditorium | 0.4
| Sunken Slab | 0.45
LIVE LOAD | Terrace accessible | 0.15
| At First Floor | 0.5
| Toilet area | 0.2